## PAG-BOQ
No. | Description | Items | CAT | CS | IT | Unit Cost | Quan. | Unit | Total | Remarks
A | FDAS
1 | Fire alarm control Panel | [5 empty] | 1 | set | 0
2 | Smoke Detectors |  | F | 5 | 4 | 2160 | 7 | units | 15120
3 | Heat Detectors |  | F | 5 | 4 | 1620 |  | units | 0
4 | Manual Pull Station |  | F | 5 | 4 | 1890 | 3 | units | 5670
5 | Horn Strobe Annunciator |  | F | 5 | 4 | 2700 | 1 | units | 2700
6 | Twisted Pair wire 2.5mm2 |  | F | 5 | 4 | 108 | 60 | lm | 6480
7 | 20mmØ IMC pipe |  | F | 5 | 4 | 540 | 15 | lm | 8100
8 | Locknut and Bushing |  | F | 5 | 4 | 10000 | 1 | lot | 10000
9 | 15mmØ FMC Conduit |  | F | 5 | 4 | 10000 | 1 | lot | 10000
10 | FMC Connectors |  | F | 5 | 4 | 1890 | 1 | pcs | 1890
11 | Junction Box |  | F | 5 | 4 | 2160 | 1 | pcs | 2160
12 | Hangers and Supports |  | F | 5 | 4 | 2000 | 1 | lot | 2000
13 | Testing and Commissioning |  | F | 5 | 4 | 10000 | 1 | lot | 10000
B | Mechanical
1 | Installations for Instrumentation/Controls | SCADA integration (Total and individual kW, V, A, PF, eff, data logger and organizer) | M | - | 6 | - | 1 | lot | 10000000 | Refer to conceptual design
2 |  | PLC integration | M | - | 6
3 |  | Flow meter at mains | M | - | 6
4 |  | Flow meter at branches (per pump) | M | - | 6
5 |  | Pressure gauge and transmitter mains | M | - | 6
6 |  | Pressure gauge and transmitter branch | M | - | 6
7 |  | Vibration monitoring probes | M | - | 6
8 |  | Motor Wind temperature sensor | M | - | 6
9 |  | Thermodynamic efficiency device | M | - | 6
10 |  | Motorization of Discharge isolation valve | M | - | 6
11 |  | MOV position sensor and actuator | M | - | 6
12 |  | Reservoir water level meter | M | - | 6
13 |  | Chlorine tank level meter | M | - | 6
14 |  | Chlorine dosage monitoring device | M | - | 6
15 |  | VFD upgrade | M | - | 6
16 | Pump performance | Pump Reconditioning | M | - | 1 | - | 1 | lot | 2000000 | See vibration analysis recommendations. Immediate attention required
17 |  | Automatic pump lubrication system upgrade | M | - | 6 | 80000 | 8 | point | 640000
18 |  | Replace existing motor with new high efficiency motors | E | - | 3 |  |  |  | 200000
19 | Building layout reconfiguration | Pump house layout reconfiguration | M | - | 4 |  |  |  | 2500000 | Improve space utilization
20 |  | Control center and operator room refubishing |  | - | 4 |  |  |  | 1000000 | Ergonomically sound Pump Station for Operator's Welfare
21 | Pipe and fitting reconfiguration and refurbishing | Adjustment of pump positions | M | - | 4 | - | 1 | lot | 3000000 | Refer to conceptual design
22 |  | Provision of straight pipe at suction side of pumps and use of eccentric FOT reducer | M | - | 4
23 |  | Relocation of valves: BV at suction and discharge, CV at discharge side only | M | - | 4
24 |  | Removal of redundancy between FJ and STC (remove STC retain FJ) | M | - | 4
25 |  | Modification of suction take off line int Y - connection (preferably at 45deg) | M | - | 4
26 |  | Replacement of defective dial pressure gauges | M | - | 4
27 |  | Replacement of defective valves | M | - | 4
28 |  | Refurbishment of corroded areas and cleaning of clogged orifices | M | - | 4
29 |  | Installation of pressure gauges at desirable points near pump | M | - | 4 |  |  |  |  | Refer to conceptual design
30 | Rehabilitation of machine foundation | Single main slab with each baseplate mounted spaced accordingly | M | - | 4 | - | 1 | lot | 1000000 | Refer to conceptual design
31 |  | Replace existing mounting with appropriate pump baseplate | M | - | 4 |  |  |  |  | Refer to conceptual design. Follow proper installation (sequence, alignment, etc.)
32 | Condition monitoring | Regular vibration analysis |  | - | 7 | 10000 | 4 | pump | 500000 | Cost considered is for long term monitoring at regular interval
33 | Reliability | Installation of additional pump (with corresponding pipes, fittings, labor and monitoring devices) | M | - | 6 | - | 1 | lot | 1000000
34 | Reservoir leakage | Additional recommendation on the reservoir (analysis and investigation regarding the structural integrity and cause of leakage, provide recommendations to the problem) | M | - | 1 | - | 1 | lot | 500000 | For analysis and investigation, rehabilitation cost not yet included
d | Lighting | Installation of lights for pump vicinity and reservoir | M | - | 6 | - | 1 | lot | 100000
22514120