## asv_visual
Item | Description | Model | Brand | Status | Remarks
1 | Main Switch/Switchboard | MDP 460V/MDP230V | Local Fabrication | 1 | Still being used
2 | Distribution Transformer | 75kVA, 460V | Wescor | 1 | Still being used
3 | Maynilad Owned Load Break Switch (LBS) | n/a | N/a | 0 | Low voltage installation
4 | Power Cables (secondary side of DT to the Elect. Loads) | THHN cables | Not visible | 1 | cable visually not maintained
5 | Motor Control Center | 230V and 460V MCC | Local Assembly | 1 | With defective components
6 | Capacitor Bank | n/a | n/a | 0 | Not found
7 | TVSS | n/a | N/a | 0 | Not found
8 | Power Meter | Analog V and A | Not visble | 1 | Pointer still moving and has reading
9 | Filters and Reactors | n/a | n/a | 0 | Not found
10 | Instrument Transformers | Current and Voltage |  | 1 | wiring acceptable
11 | Electrical Protective Relays | n/a | n/a | 0 | Not found
12 | Motor and Switches | Nameplate blurred | nameplate blurred | 1 | Nameplate already blurred
13 | Transfer Switch | Automatic | Synchrogen | 1 | Functioning as Manual Transfer
| Transfer Switch | Manual | n/a | 1 | Not functioning; not used
14 | Uninterruptible Power System (UPS) | n/a | n/a | 0 | Not found
15 | Distrbution Panelboards and assoc. appurtenances | DP and LPB | locally fabricated | 1 | Breakers are obsolete
16 | Ground-Fault Circuit Interrupter (GFCI) or ELCB or (RCD) | n/a | n/a | 0 | Not found
17 | Lighting and Lighting Control System | 1x40 lighting fixture | Not visbile | 1 | w/ non-functioning fixtures
18 | Emergency Generator | Standby Genset | Cumper | 1 | Rusted enclosure
19 | Building Service and Distribution | utility owned | Not visbile | 1 | Open delta connection

## asv_short circuit
Item | Description | SCC (kA) | Kaic \& CB (kA) | REMARKS
1 | From Utility to tansformer | 8.357 | Utility owned trafo | Protection c/o Utility
2 | Pole Mounted transformer to main disconnect switch | 1.295 | Rating of CB is 400A per nameplate | Cover of MDS stuck. Advised not to open due to arc flash
3 | Main disconnect switch 400A to Automatic transfer switch panel | 1.266 | Rating not visible | n/a
4 | Automatic transfer switch panel to MDP_P 460V | 1.258 | 35 | Existing acceptable
5 | MDP-P 460V to Enclosed CB 200A | 1.233 | 25 | Existing acceptable
6 | Enclosed CB 200A to dry type transformer 112.5 kVA | 1.882 | 25 | Upstream protection is ECB 200A
7 | Dry type transformer 112.5 kVA to MDP-S 230V | 1.781 | 42 | Existing acceptable
8 | MDP-S 230V to MCC 230V | 1.781 | 65 | Existing acceptable
9 | MDP-P 460V to MCC 460V | 1.254 | 65 | Existing acceptable
10 | MDP-P 460V to MCC 440V | 1.248 | 35 | Existing acceptable
11 | MDP-P 460V to dry type transformer 75kVA | 1.252 | None | N/a
12 | Dry type transformer 75 kVA to Enclosed CB 150A | 1.862 | 22 | Existing acceptable
13 | Enclosed CB 150A to Lighting Panel | 1.754 | 10 | Existing acceptable

## vdc
VOLTAGE DROP SUMMARY COMPUTATION
AYALA SOUTHVALE PUMP STATION
FEEDER CABLES VOLTAGE DROP
Item | From | To | Wire Size, mm² | I | Length Meters | R Ω/305m | X Ω/305m | VD | %VD | REMARKS
1 | Pole Mounted Transformer 50kVA | Main Disconnect Switch | 250 | 425 | 21 | 0.048 | 0.027 | 2.788 | 0.5808% | Within Limits
2 | Main Disconnect Switch 400 | ATS PANEL | 250 | 425 | 35 | 0.048 | 0.027 | 4.6466 | 0.9681% | Within Limits
3 | ATS PANEL | MDP-P 460V | 250 | 425 | 7.464 | 0.048 | 0.027 | 0.99093 | 0.2064% | Within Limits
4 | MDP-P 460V | MCC 1 | 250 | 425 | 3.56 | 0.048 | 0.027 | 0.2732 | 0.05692% | Within Limits
5 | MDP-P 460V | MCC 2 | 250 | 425 | 6 | 0.048 | 0.027 | 0.79657 | 0.166% | Within Limits
6 | MDP-P 460V | ECB 200A | 250 | 425 | 9 | 0.048 | 0.027 | 0.69067 | 0.1439% | Within Limits
7 | ECB 200A | DRY TYPE TRANSFORMER 112.5KVA | 125 | 285 | 2 | 0.057 | 0.052 | 0.24945 | 0.05197% | Within Limits
8 | DRY TYPE TRANSFORMER 112.5KVA | MDP-S 230V | 125 | 285 | 20.5 | 0.057 | 0.052 | 2.5569 | 1.112% | Within Limits
9 | MDP-S 230V | MCC 230V | 125 | 285 | 1 | 0.057 | 0.052 | 0.12473 | 0.05423% | Within Limits
10 | MDP-P 460V | DRY TYPE TRANSFORMER 75KVA | 250 | 425 | 4.5 | 0.063 | 0.051 | 0.87929 | 0.2198% | Within Limits
11 | DRY TYPE TRANSFORMER 75KVA | LP PANEL | 60 | 170 | 9 | 0.1 | 0.054 | 0.98628 | 0.4288% | Within Limits

## asv_Alert settings
Table: Percentage Alert Settings
Table 1.6.1

## asv_Total Generation
Table : Summary of Total Generation, Loading & Demand

## asv_Branch Loading
Table: 1. 9: Branch Loading Summary Report

## asv_Bus loading
Table 1.8: Bus loading

## asv_harmonic study
Table 1.13 Harmonic Study
Table 1.17 Power Quality - Total Harmonic Distortion Compliance
TOTAL HARMONIC DISTORTION (%) | PHASE | MINIMUM | AVERAGE | MAXIMUM | LIMITS (5%) | REMARKS
MAIN 200A | AB | 3.89 | 3.93 | 4.94
(Load Side) | BC | 3.58 | 3.6 | 4.68 | ≤ 5% | WITHIN LIMITS
| CA | 3.89 | 3.93 | 4.94
| AB | 4.54 | 4.58 | 4.79
VFD-1 | BC | 4 | 4.07 | 4.31 | ≤ 5% | WITHIN LIMITS
| CA | 4.54 | 4.58 | 4.79
| AB | 2.86 | 4.01 | 4.38
Softstarter | BC | 2.68 | 3.62 | 3.86 | ≤ 5% | WITHIN LIMITS
| CA | 2.86 | 4.01 | 4.38

## asv_TDD
Table 1.18 Power Quality - Total Demand Distortion Compliance
TOTAL DEMAND DISTORTION (%) | PHASE | MINIMUM | AVERAGE | MAXIMUM | LIMITS (5%) | REMARKS
MAIN 200A | AB | 18.23 | 15.66 | 62.39 |  |  | 0.1823 | 0.1566 | 0.6239
(Load Side) | BC | 1.09 | 1.15 | 22.33 | ≤ 5% | Outside limits | 0.0109 | 0.0115 | 0.2233
| CA | 17.9 | 16.57 | 60.13 |  |  | 0.179 | 0.1657 | 0.6013
| AB | 15.73 | 15.9 | 41.79 |  |  | 0.1573 | 0.159 | 0.4179
VFD-1 | BC | 2.88 | 3.47 | 6.79 | ≤ 5% | Outside limits | 0.0288 | 0.0347 | 0.0679
| CA | 16.58 | 16.89 | 25.48 |  |  | 0.1658 | 0.1689 | 0.2548
| AB | 9.25 | 13.67 | 44.67 |  |  | 0.0925 | 0.1367 | 0.4467
Softstarter | BC | 1.84 | 2.46 | 83.07 | ≤ 5% | Outside limits | 0.0184 | 0.0246 | 0.8307
| CA | 8.61 | 12.55 | 30.98 |  |  | 0.0861 | 0.1255 | 0.3098

## asv_rms voltage
Table 1.14 RMS Voltage Compliance
RMS VOLTAGE (460 VOLTS) | Phase | Minimum | Average | MAXIMUM | LIMITS | REMARKS
MAIN 200A | AB | 441.18 | 468 | 472.86
(Load Side) | BC | 438.68 | 464.4 | 469.7 | ±10\% (414-506V) | WITHIN LIMITS
| CA | 441.18 | 468 | 472.86
| AB | 443.84 | 467.7 | 472.96
VFD-1 | BC | 441.76 | 463.5 | 468.26 | ±10\% (414-506V) | WITHIN LIMITS
| CA | 443.84 | 467.7 | 472.96
| AB | 441.71 | 458.5 | 463.26
Softstarter | BC | 439.34 | 456 | 459.5 | ±10\% (414-506V) | WITHIN LIMITS
| CA | 441.71 | 458.5 | 463.26

## asv_voltage unbalance
Table 1.15 Voltage Unbalance Compliance
Voltage Unbalance | MINIMUM Deviation | AVERAGE Deviation | MAXIMUM Deviation | LIMITS (%) | REMARKS
MAIN 200A (Load Side) | 0.38 | 0.51 | 0.45 | ±2.5% | WITHIN LIMITS
VFD-1 | 0.31 | 0.6 | 0.66 | ±2.5% | WITHIN LIMITS
Softstarter | 0.36 | 0.36 | 0.54 | ±2.5% | WITHIN LIMITS

## asv_Frequency
Table 1.19 Frequency Compliance
Frequency (Hz) | MINIMUM | AVERAGE | MAXIMUM | LIMITS | REMARKS
MAIN 200A (Load Side) | 59.476 | 60.14 | 60.423 | 59.7-60.3 | Outside limits
VFD-1 | 59.734 | 60.06 | 60.405 | 59.7-60.3 | Outside limits
Softstarter | 59.721 | 60.06 | 60.328 | 59.7-60.3 | Within limits

## asv_flicker
Table 1.21 Flicker Compliance
Flicker | Parameter | AB | BC | CA | LIMITS | REMARKS
MAIN 200A | Plt | 0.431 | 0.405 | 0.534 | ≤0.8 | Within Limits
(Load Side) | Pst | 0.879 | 0.787 | 1.071 | ≤1.0 | Outside Limits
| Plt | 0.284 | 0.293 | 0.371 | ≤0.8 | Within Limits
VFD-1 | Pst | 0.568 | 0.587 | 0.76 | ≤1.0 | Within Limits
| Plt | 0.134 | 0.145 | 0.159 | ≤0.8 | Within Limits
Softstarter | Pst | 0.545 | 0.532 | 0.7 | ≤1.0 | Within Limits

## asv_power factor
Table 1.20 Power Factor Compliance
Power Factor | MINIMUM | AVERAGE | MAXIMUM | LIMITS (%) | REMARKS
MAIN 200A (Load Side) | 0.9 | 0.9 | 0.9 | >0.85% | WITHIN LIMITS
VFD-1 | 0.53 | 0.53 | 0.58 | >0.85% | Outside limits
Softstarter | 0.89 | 0.91 | 0.91 | >0.85% | WITHIN LIMITS

## asv_grounding
GROUNDING RESISTANCE MEASUREMENT TEST
SUMMARY OF FINDNGS
LOCATION | EQUIPMENT NAME /ROOM | MEASURED GROUNDING RESISTANCE | FINDINGS | RECCOMMENDATIONS | EFFECTS | RISKS
[5 empty] | IF NOT CORRECTED | (POSSIBLE OUTCOME)
ECB OUTDOOR | TEST POINT 1 BARE COPPER WIRE | NO DATA | BCW WAS SUBMERGED IN WATER | REMOVE WATER AND ESTABLISH GROUNDING CONNECTION TO ATS | (1) Unwanted voltage maybe present on non-current carrying metal objects (2) Equipment might be damaged during a fault condition | (1) Incorrect Operation of overcurrent device with ground fault protection (2) Health and safety risks for facilities and personnel
ATS EQUIPMENT GROUND | TEST POINT 1 COPPER WIRE | 0.62Ω | Within the 5 ohms limit as per NFPA and IEE standards | None | None | None
GENSET GROUND | TEST POINT 2 GROUND ROD | 8.01Ω | (1) Already exceeds the 5 ohms limits as per NFPA and IEE standards | (1) Checking and retightening of loose grounding terminal connections (2) Replacement of improper lugs for grounding terminations | (1) Overheating on conductors and possible nuisance tripping of ground fault protection or relays | Damage to equipment or accessories
PANELBOARD 460V | TEST POINT 1 BARE COPPER WIRE | NO DATA | CONNECTED TO BCW SUBMERGED IN WATER. | REMOVE WATER AND ESTABLISH GROUNDING CONNECTION TO ATS | (1) Unwanted voltage maybe present on non-current carrying metal objects (2) Equipment might be damaged during a fault condition | (1) Incorrect Operation of overcurrent device with ground fault protection (2) Health and safety risks for facilities and personnel
PANELBOARD 400V | TEST POINT 1 BARE COPPER WIRE | NO DATA | CONNECTED TO BCW SUBMERGED IN WATER. | REMOVE WATER AND ESTABLISH GROUNDING CONNECTION TO ATS | (1) Unwanted voltage maybe present on non-current carrying metal objects (2) Equipment might be damaged during a fault condition | (1) Incorrect Operation of overcurrent device with ground fault protection (2) Health and safety risks for facilities and personnel
PANELBOARD 230V | TEST POINT 1 BARE COPPER WIRE | NO DATA | CONNECTED TO BCW SUBMERGED IN WATER. | REMOVE WATER AND ESTABLISH GROUNDING CONNECTION TO ATS | (1) Unwanted voltage maybe present on non-current carrying metal objects (2) Equipment might be damaged during a fault condition | (1) Incorrect Operation of overcurrent device with ground fault protection (2) Health and safety risks for facilities and personnel
Locations | Asset/Room | Resistance | FINDINGS | Recommendations | Effects | Risks
ECB OUTDOOR | TEST POINT 1 BARE COPPER WIRE | NO DATA | BCW WAS SUBMERGED IN WATER | REMOVE WATER AND ESTABLISH GROUNDING CONNECTION TO ATS | (1) Unwanted voltage maybe present on non-current carrying metal objects (2) Equipment might be damaged during a fault condition | (1) Incorrect Operation of overcurrent device with ground fault protection (2) Health and safety risks for facilities and personnel
ATS EQUIPMENT GROUND | TEST POINT 1 COPPER WIRE | 0.62$\Omega$ | Within the 5 ohms limit as per NFPA and IEE standards | None | None | None
GENSET GROUND | TEST POINT 2 GROUND ROD | 8.01\Omega$ | (1) Already exceeds the 5 ohms limits as per NFPA and IEE standards | (1) Checking and retightening of loose grounding terminal connections (2) Replacement of improper lugs for grounding terminations | (1) Overheating on conductors and possible nuisance tripping of ground fault protection or relays | Damage to equipment or accessories
PANELBOARD 460V | TEST POINT 1 BARE COPPER WIRE | NO DATA | CONNECTED TO BCW SUBMERGED IN WATER. | REMOVE WATER AND ESTABLISH GROUNDING CONNECTION TO ATS | (1) Unwanted voltage maybe present on non-current carrying metal objects (2) Equipment might be damaged during a fault condition | (1) Incorrect Operation of overcurrent device with ground fault protection (2) Health and safety risks for facilities and personnel
PANELBOARD 400V | TEST POINT 1 BARE COPPER WIRE | NO DATA | CONNECTED TO BCW SUBMERGED IN WATER. | REMOVE WATER AND ESTABLISH GROUNDING CONNECTION TO ATS | (1) Unwanted voltage maybe present on non-current carrying metal objects (2) Equipment might be damaged during a fault condition | (1) Incorrect Operation of overcurrent device with ground fault protection (2) Health and safety risks for facilities and personnel
PANELBOARD 230V | TEST POINT 1 BARE COPPER WIRE | NO DATA | CONNECTED TO BCW SUBMERGED IN WATER. | REMOVE WATER AND ESTABLISH GROUNDING CONNECTION TO ATS | (1) Unwanted voltage maybe present on non-current carrying metal objects (2) Equipment might be damaged during a fault condition | (1) Incorrect Operation of overcurrent device with ground fault protection (2) Health and safety risks for facilities and personnel

## asv_arc flash
FLASH HAZARD RISK CATEGORY | RANGE OF CALCULATED INCIDENT ENERGY [cal/cm2] | MINIMUM PPE RATING [cal/cm2] | CLOTHING REQUIRED
0 | 0 ≤E ≤1.2 | N/A | 4.5-14.0 oz/yd2untreated cotton
1 | 1.2 < E ≤ 4 | 4 | Flame Retardant (FR) shirt and Pants
2 | 4 < E ≤ 8 | 8 | Cotton underclothing plus FR shirt and pants
3 | 8 < E ≤ 25 | 25 | Cotton underclothing plus FR shirt, pants, overalls or equivalent
4 | 25 < E ≤ 40 | 40 | Cotton underclothing plus FR shirt, pants, plus double layer switching coat and pants or equivalent
5 | 40 < E ≤ 100 | 100 | Cotton underclothing plus FR shirt, pants, plus multi-layer switching suit or equivalent

## asv_current_unbalance
Table 1.1 Current Unbalance Compliance
Current Unbalance | MINIMUM Deviation | AVERAGE Deviation | MAXIMUM Deviation | LIMITS (%) | REMARKS
MAIN 200A (Load Side) | 13.07 | 8.73 | 6.74 | ±10% | Outside Limits
VFD-1 | 77.36 | 8.73 | 6.47 | ±10% | Outside Limits
Softstarter | 13.72 | 9.71 | 6.74 | ±10% | Outside Limits

## asv_voltagedrop
VOLTAGE DROP SUMMARY COMPUTATION
AYALA SOUTHVALE PUMP STATION
FEEDER CABLES VOLTAGE DROP
Item | From | To | Wire Size, mm² | I | Length Meters | R Ω/305m | X Ω/305m | VD | %VD | REM
1 | Pole Mounted Transformer 50kVA | Main Disconnect Switch | 250 | 425 | 21 | 0.048 | 0.027 | 2.788 | 0.58083 | Within Limits | 0.0058083
2 | Main Disconnect Switch 400 | ATS PANEL | 250 | 425 | 35 | 0.048 | 0.027 | 4.6466 | 0.96805 | Within Limits | 0.0096805
3 | ATS PANEL | MDP-P 460V | 250 | 425 | 7.464 | 0.048 | 0.027 | 0.99093 | 0.20644 | Within Limits | 0.0020644
4 | MDP-P 460V | MCC 1 | 250 | 425 | 3.56 | 0.048 | 0.027 | 0.2732 | 0.056916 | Within Limits | 0.00056916
5 | MDP-P 460V | MCC 2 | 250 | 425 | 6 | 0.048 | 0.027 | 0.79657 | 0.16595 | Within Limits | 0.0016595
6 | MDP-P 460V | ECB 200A | 250 | 425 | 9 | 0.048 | 0.027 | 0.69067 | 0.14389 | Within Limits | 0.0014389
7 | ECB 200A | DRY TYPE TRANSFORMER 112.5KVA | 125 | 285 | 2 | 0.057 | 0.052 | 0.24945 | 0.051969 | Within Limits | 0.00051969
8 | DRY TYPE TRANSFORMER 112.5KVA | MDP-S 230V | 125 | 285 | 20.5 | 0.057 | 0.052 | 2.5569 | 1.1117 | Within Limits | 0.011117
9 | MDP-S 230V | MCC 230V | 125 | 285 | 1 | 0.057 | 0.052 | 0.12473 | 0.054229 | Within Limits | 0.00054229
10 | MDP-P 460V | DRY TYPE TRANSFORMER 75KVA | 250 | 425 | 4.5 | 0.063 | 0.051 | 0.87929 | 0.21982 | Within Limits | 0.0021982
11 | DRY TYPE TRANSFORMER 75KVA | LP PANEL | 60 | 170 | 9 | 0.1 | 0.054 | 0.98628 | 0.42882 | Within Limits | 0.0042882

## Sheet1
Protective Device Settings - Low Voltage Circuit Breaker with Thermal-Magnetic Trip Device
LVCB ID | Manufacturer | Breaker |  | Thermal |  | Magnetic (Inst.)
|  | Model | Size | Setting | Trip | Setting | Trip
[5 empty] | (Amps) |  | (Amps)
CB3 | Siemens | Sentron JFC | 500 | Fixed | 500 | Fixed | xIn
CB12 | Siemens | Sentron JFC | 400 | Fixed | 400 | Fixed | xIn
CB11 | Siemens | CQD | 100 | Fixed | 100 | Fixed | xIn
CB6 | GE | QB | 225 | Fixed | 225 | Fixed | xIn
CB10 | GE | QJ | 150 | Fixed | 32 | Fixed | xIn
CB5 | GE | EDNC | 200 | Fixed | 200 | Fixed | xIn
CB7 | Schneider | NS | 225 | Fixed | 225 | Fixed | xIn