## CHE-Visual Inspection
Item | Categories | Asset name | Model | Branch | Status | CS | Remarks
1 | Main switch/Switch board |  |  |  | 0
2 | Distribution transformer | 150 Kva Transformer (Utility Supply)) |  |  | 1 | 1
3 | Maynilad owned Load Break Switch (LBS) |  |  |  | 0
4 | Power cables |  |  |  | 1 | 1 | Not visually observed
5 | MCC | Moulded Case Circuit Breakers | Bw400Eag, Bw125Jag | Fuji, |  | 1
| MCC | Uninterruptible Power Supply
| MCC | Variable Frequency Drive | Vlt Aqua Drive | Danfoss
| MCC | Miniature Circuit Breakers |  | Fuji, Schneider
| MCC | Magnetic Contactors | Sc-N2S
6 | Capacitor bank |  |  |  | 0
7 | TVSS | Surge Protection Device |  | Protec | 1 | 1
8 | Power meter | Kilowatthour Meter | V-62S | Canadian General Elect. | 1 | 1
9 | Filter and Reactors | Harmonic Filter, 70Amps | Vlt | Danfoss | 1 | 1
10 | Instrument Transformer | Current Transformers |  |  | 1 | 1
11 | Electrical Protective Relays |  |  |  | 1 | 1
12 | Motors and Switches |  |  |  |  | 1
13 | Transfer Switch | Manual Transfer Switch | Bw400Eag | Fuji | 1 | 1
14 | Uninterruptible power system (UPS) and batteries
15 | Distribution panel boards and associated appurtenances
16 | Ground-fault circuit Interrupter (GFCI) or Electric leakage circuit breaker (ELCB) or Residual Circuit Devices (RCD) | [6 empty] | HHDHHFFD
17 | Emergency Generator | Silent Diesel Generator110Kva/88Kw, 220/440V, 60Hz | Hgc-80 | Hexagen | 1 |  |  | Hhdhhffd
18 | Building Service and Distribution
|  | Lightning Arrester With Counter | Cdr-401 | Cirprotec | 1

## CHE-SCC
Item | Description | SCC (Ka) | Kaic \& Cb (Ka) | CS | IT | Remarks | Item | Description | Scc (Ka) | Kaic \& Cb (Ka) | Remarks
A. | Three Phase |  |  | 1 | 1 |  | A. | Three Phase
1 | 3 X 50 Kva Transformer-Secondary | 2.479 | - | 1 | 1 | Protection Via Fuse Provided By Utility | 1 | 3 X 50 Kva Transformer-Secondary | 2.479 | - | Protection Via Fuse Provided By Utility
2 | Transfer Swtich | 2.418 | 18 | 1 | 1 | Existing Acceptable | 2 | Transfer Swtich | 2.418 | 18 | Existing Acceptable
3 | Main Mccb 250A @460 | 2.418 | 18 | 1 | 1 | Existing Acceptable | 3 | Main Mccb 250A @460 | 2.418 | 18 | Existing Acceptable
|  |  |  | 1 | 1
4 | Feeder Mccb-1 100A (30Hp Motor) | 2.391 | 8 | 1 | 1 | Existing Acceptable | 4 | Feeder Mccb-1 100A (30Hp Motor) | 2.391 | 8 | Existing Acceptable
5 | Feeder Mccb-2 100A (30Hp Motor) Alternate | 2.391 | 8 | 1 | 1 | Existing Acceptable | 5 | Feeder Mccb-2 100A (30Hp Motor) Alternate | 2.391 | 8 | Existing Acceptable
6 | Motorized Opening Valve Supply 1 | 2.391 | 8 | 1 | 1 | Existing Acceptable | 6 | Motorized Opening Valve Supply 1 | 2.391 | 8 | Existing Acceptable
7 | Motorized Opening Valve Supply 2 | 2.391 | 8 | 1 | 1 | Existing Acceptable | 7 | Motorized Opening Valve Supply 2 | 2.391 | 8 | Existing Acceptable
8 | Motor1 -30Hp | 0.143 | - | 1 | 1 | Protection Via Vfd | 8 | Motor1 -30Hp | 0.143 | - | Protection Via Vfd
9 | Motor2-30 Hp | - | - | 1 | 1 | Alternate | 9 | Motor2-30 Hp | - | - | Alternate
B | Single Phase | [5 empty] | B | Single Phase
1 | Mccb 30A | 2.041 | 2.5 | 1 | 1 | Existing Acceptable | 1 | Mccb 30A | 2.041 | 2.5 | Existing Acceptable
2 | Dry Type Transformer 2.5 Kva | 0.411 | - | 1 | 1 | Protection Via Upstream Mccb | 2 | Dry Type Transformer 2.5 Kva | 0.411 | - | Protection Via Upstream Mccb
3 | Mcb 32A Ups (Lump 3) | 0.3964 | 2.5 | 1 | 1 | Existing Acceptable | 3 | Mcb 32A Ups (Lump 3) | 0.3964 | 2.5 | Existing Acceptable
4 | Mcb 32A Light & Conv Outlet (Lump 4) | 0.394 | 2.5 | 1 | 1 | Existing Acceptable | 4 | Mcb 32A Light & Conv Outlet (Lump 4) | 0.394 | 2.5 | Existing Acceptable
5 | Mcb 32A For Meter (Lump 5) | 0.394 | 2.5 | 1 | 1 | Existing Acceptable | 5 | Mcb 32A For Meter (Lump 5) | 0.394 | 2.5 | Existing Acceptable

## CHE-VDC
Item | From | To | Wire Size | I | L | R | X | Vd | \%Vd | Remarks | Item | From | To | Wire Size, mm² | I | Length Meters | R Ω/305m | X Ω/305m | VD | %VD | REMARKS
|  |  | $mm^2$ | Ampe | m | $\Omega$/305 m | $\Omega$/305 m
1 | Pole Mounted Transformer 50Kva,3 $\Phi$ | Ats Panel | 250 | 425 | 15.52 | 0.048 | 0.027 | 2.06 | 0.0043 | Within Limits | 1 | Pole Mounted Transformer 50kVA,3Ø | ATS PANEL | 250 | 425 | 15.52 | 0.048 | 0.027 | 2.06 | 0.43% | WITHIN LIMTS
2 | Mts Panel | Ecb 250A | 250 | 425 | 7 | 0.048 | 0.027 | 0.929 | 0.0019 | Within Limits | 2 | MTS PANEL | ECB 250A | 250 | 425 | 7 | 0.048 | 0.027 | 0.929 | 0.19% | WITHIN LIMTS
3 | Ecb 30A, 2P | Dry Type Transformer 2.5Kva | 5.5 | 40 | 4.2 | 1.2 | 0.063 | 1.324 | 0.0055 | Within Limits | 3 | ECB 30A, 2P | DRY TYPE TRANSFORMER 2.5KVA | 5.5 | 40 | 4.2 | 1.2 | 0.063 | 1.324 | 0.55% | WITHIN LIMTS
4 | Dry Type Transformer 2.5Kva, 1$\Phi$ | Ups Panel | 5.5 | 40 | 4 | 1.2 | 0.063 | 1.261 | 0.0053 | Within Limits | 4 | DRY TYPE TRANSFORMER 2.5KVA, 1Ø | UPS PANEL | 5.5 | 40 | 4 | 1.2 | 0.063 | 1.261 | 0.53% | WITHIN LIMTS
5 | Mccb 100A, 3P | 30Hp Motor | 30 | 115 | 10 | 0.2 | 0.057 | 1.357 | 0.0028 | Within Limits | 5 | MCCB 100A, 3P | 30HP MOTOR | 30 | 115 | 10 | 0.2 | 0.057 | 1.357 | 0.28% | WITHIN LIMTS
| Pole mounted to 30 HP motor | [6 empty] | 3.417 | 0.71 | Within Limits

## CHE-Load Flow Study
Summary of total generation, loading, and demand

## CHE-Protection-Coordination
Protective Device Settings - Low Voltage Circuit Breaker with Thermal-Magnetic Trip Device | [7 empty] | Items | Protective Device |  |  | Cable Protection |  |  |  | Max Fault 3Ph-Amps | Refe-rence kV | Zone |  | Stream |  | Max Fault |  | Ref. | Coord. | Amp Range |  | Condition
LVCB ID | Manufacturer | Breaker |  | Thermal |  | Magnetic (Inst.) |  |  | Location | ID | Type | Pickup Limit | Ampacity | Damage Curve | Condition |  |  | ID | type | up | down | type | Amp | kV | status | From | To
|  | Model | Size | Setting | Trip | Setting | Trip | Cable1 | Load | CB1 | TM-Magnetic | - | - | Pass | Trip curve protects the damage curve | 2418 | 0.48 |  |  | PD | PD
[5 empty] | (Amps) |  | (Amps) |  |  |  | TM-Thermal | Pass | Pass | Pass | Therm. Trip 250 A is within 302.7 A = Ampacity |  |  | Bus4 | Bus | CB4 | CB9 | 3Ph | 2391 | 0.48 | Alert | 2000 | 2000 | Miscoordination, the time gap is smaller than 0.001 sec margin at I=2000 A, Plot Ref. kV=0.48
CB4 | Fuji Electric | BW400EAG | 250 | Fixed | 250 | Fixed | 8 xIn | [7 empty] | Therm. Trip 250 A is within max. limit of 302.7 A = Ampacity x 100\% | [6 empty] | L-G |  |  | Warning |  |  | L-G fault coordination is not possible.
CB9 | Fuji Electric | BW125JAG | 100 | Fixed | 100 | Fixed | 8 xIn | [7 empty] | Trip curve protects the damage curve | [5 empty] | CB11 | 3Ph | 2391 | 0.48 | Alert | 2000 | 2000 | Miscoordination, the time gap is smaller than 0.001 sec margin at I=2000 A, Plot Ref. kV=0.48
CB10 | Fuji Electric | BW125JAG | 100 | Fixed | 100 | Fixed | 8 xIn | Cable3 | Load | CB4 | TM-Magnetic | - | - | Pass | Trip curve protects the damage curve | 2391 | 0.48 |  |  |  |  | L-G |  |  | Warning |  |  | L-G fault coordination is not possible.
CB11 | Fuji Electric | BW32SAG | 32 | Fixed | 32 | Fixed | 8 xIn |  |  |  | TM-Thermal | Pass | Pass | Pass | Therm. Trip 250 A is within 302.7 A = Ampacity | [5 empty] | CB12 | 3Ph | 2391 | 0.48 | Alert | 2000 | 2000 | Miscoordination, the time gap is smaller than 0.001 sec margin at I=2000 A, Plot Ref. kV=0.48
CB12 | Fuji Electric | BW32SAG | 32 | Fixed | 32 | Fixed | 8 xIn | [7 empty] | Therm. Trip 250 A is within max. limit of 302.7 A = Ampacity x 100\% | [6 empty] | L-G |  |  | Warning |  |  | L-G fault coordination is not possible.
CB1 | Fuji Electric | BW400EAG | 250 | Fixed | 250 | Fixed | 8 xIn | [7 empty] | Trip curve protects the damage curve | [5 empty] | CB10 | 3Ph | 2391 | 0.48 | Alert | 2000 | 2000 | Miscoordination, the time gap is smaller than 0.001 sec margin at I=2000 A, Plot Ref. kV=0.48
[22 empty] | L-G |  |  | Warning |  |  | L-G fault coordination is not possible.

## CHE-Harmonic
Total Harmonic Distortion | Phase | Minimum | Average | Maximum | Limits | Comments
(\%) |  |  |  |  | (5\%)
Main 250A (Load side) | Ab | 1.44 | 3.36 | 3.9
| Bc | 1.27 | 2.56 | 2.86 | 5 | Within Limits
| Ca | 1.53 | 3.36 | 3.9
VFD-1 | Ab | 3.22 | 3.36 | 3.9
| Bc | 2.89 | 3.01 | 3.37 | 5 | Within Limits
| Ca | 3.22 | 3.36 | 3.9
VFD-2 | Ab | 2.11 | 2.2 | 2.68 | 5 | Within Limits
PARAMETER | PHASE | MINIMUM | AVERAGE | MAXIMUM | LIMITS | COMMENTS
TOTAL HARMONIC DISTORTION | AB | 3.22 | 3.36 | 3.9
| BC | 2.89 | 3.01 | 3.37 | 5% | WITHIN LIMITS
| CA | 3.22 | 3.36 | 3.9
PARAMETER | PHASE | MINIMUM | AVERAGE | MAXIMUM | LIMITS | COMMENTS
TOTAL HARMONIC DISTORTION (%) | AB | 2.11 | 2.2 | 2.68
[5 empty] | 5% | WITHIN LIMITS

## CHE-powerquality
RMS Voltage compliance
RMS VOLTAGE | Phase | Minimum | Average | Maximum | Limits | Remarks | Remarks
(460 VOLTS)
Main 250A (Load side) | AB | 449.94 | 465.3 | 474.84
| BC | 457.72 | 471.4 | 477.32 | ±10\% (414-506V) | Within Limits
| CA | 449.94 | 465.3 | 474.84
VFD-1 | AB | 449.68 | 460.18 | 474.76
| BC | 387.66* | 408.04 | 468.34 | ±10\% (414-506V) | Outside Limits | Value reached voltage limitation
| CA | 449.68 | 460.18 | 474.76
VFD-2 | AB | 455.48 | 466.18 | 474.7
| BC | 463.28 | 470.61 | 477.76 | ±10\% (414-506V) | Within Limits
| CA | 455.48 | 466.18 | 474.7
Volrage unbalance
Volrage unbalance | Phase | Minimum | Average | Maximum | Limits | Remarks
(\%)
Main 250A (Load side) |  | 1.15 | 0.87 | 0.35 | 2.5 | Within Limits
VFD-1 |  | 9.64 | 7.85 | 0.91 | 2.5 | Outside limits
VFD-2 |  | 1.14 | 0.63 | 0.43 | 2.5 | Within Limits
Current unbalance compliance
Current unbalance | Phase | Minimum | Average | Maximum | Limits | Remarks
(\%)
Main 250A (Load side) | AB | 0.3 | 0.7 | 2.3
| BC | 0.4 | 0.7 | 0.8 | \leq 10\% | Within Limits
| CA | 0.1 | 0.5 | 1.5
| Overall | 1.15 | 1.2 | 2.68
VFD-1 | AB | 1.33 | 1.6 | 2.57
| BC | -0.27 | -0.7 | -0.73 | \leq 10\% | Outside Limits
| CA | -1.07 | -0.9 | -1.83
| Overall | 3.4 | 3.88 | 4.6
VFD-2 | AB | 0.5 | -0.23 | 0.9
| BC | -0.2 | -0.23 | -0.3 | \leq 10\% | Within Limits
| CA | -0.3 | -0.33 | -0.6
| Overall | 2.18 | 1.36 | 2.83
THD compliance
THD compliance | Phase | Minimum | Average | Maximum | Limits | Remarks
(\%)
Main 250A (Load side) | AB | 1.44 | 3.36 | 3.9
| BC | 1.27 | 2.56 | 2.86 | \leq 5\% | Within Limits
| CA | 1.53 | 3.36 | 3.9
VFD-1 | AB | 3.22 | 3.36 | 3.9
| BC | 2.89 | 3.01 | 3.37 | \leq 5\% | Within Limits
| CA | 3.22 | 3.36 | 3.9
VFD-2 | AB | 2.11 | 2.2 | 2.68
| BC | 1.63 | 1.68 | 1.97 | \leq 5\% | Within Limits
| CA | 2.11 | 2.2 | 2.68
TDD compliance
TDD compliance | Phase | Minimum | Average | Maximum | Limits | Remarks
(\%)
Main 250A (Load side) | AB | 4.98 | 15.38 | 39.19
| BC | 5.24 | 15.77 | 41.65 | $\leq$ 5\% | Outside limits
| CA | 4.94 | 15.38 | 194.09
VFD-1 | AB | 2.42 | 15.14 | 45.33
| BC | 2.51 | 15.65 | 46.45 | $\leq$ 5\% | Outside limits
| CA | 2.3 | 15.12 | 193.54
VFD-2 | AB | 17.88 | 19.76 | 46.72
| BC | 18.62 | 20.69 | 45.28 | $\leq$ 5\% | Outside limits
| CA | 18.36 | 20.59 | 73.81
Frequency complianec
Frequency | Phase | Minimum | Average | Maximum | Limits | Remarks
|  | HZ | HZ | HZ | HZ
Main 250A (Load side) |  | 59.71 | 60.07 | 60.3 | 59.7-60.3 | Within Limits
VFD-1 |  | 59.71 | 60.1 | 60.3 | 59.7-60.3 | Within Limits
VFD-2 |  | 59.68 | 60.06 | 60.3 | 59.7-60.3 | Within Limits
Power factor
Power factor | Phase | Minimum | Average | Maximum | Limits | Remarks
Main 250A (Load side) |  | 0.86 | 0.92 | 0.93 | >0.85 | Within Limits
VFD-1 |  | 0.75 | 0.89 | 0.9 | >0.85 | Outside limits
VFD-2 |  | 0.21 | 0.92 | 0.92 | >0.85 | Outside limits
Flicker
Flicker | Parameter | Minimum | Average | Maximum | Limits | Remarks
Main 250A (Load side) | Plt | 0.194 | 0.192 | 0.183 | <=0.80 | Within Limits
| Pst | 0.262 | 0.261 | 0.237 | <=1.0
VFD-1 | Plt | 0.257 | 0.711 | 1.829 | <=0.80 | Outside limits
| Pst | 0.365 | 1.62 | 4.186 | <=1.0
VFD-2 | Plt | 0.202 | 0.185 | 0.195 | <=0.80 | Within Limits
| Pst | 0.239 | 0.234 | 0.325 | <=1.0
Crest factor
|  | Main | VOLTAGE |  | CURRENT
|  | Phase | MIN | MAX | MIN | MAX
|  | A | 1.41 | 1.44 | 1.42 | 3.27
|  | B | 141 | 1.43 | 1.39 | 2.87
|  | C | 1.41 | 1.43 | 1.4 | 7.22

## CHE-Ground
Locations | Asset/Room | Resistance | FINDINGS | Recommendations | Effects | Risks
Lightning Arrester Post | Test Point 1 Bare Copper Wire | 1.24 Ω | Within The 5 Ohms Limit As Per Nfpa And Ieee Standards | (1)Check Tightness Of Connection Of Bcw To Ground Rod | None | None
(2) Grounding System Electrical And Mechanical Connections Should Be Free Of Corrosion.
(3) Replace Bcw For Better Conductivity.
Mts Equipment Ground | Test Point 2 Bare Copper Wire | 7.2 V | Measured Voltage In The Bare Copper Wire | Check And Trace Where The Voltage Is Coming From And Correct The Connection | Danger To Personnel And Damage To Equipment If Not Immediately Corrected | Health And Safety Risks For Facilities And Personnel And Damage To Equipment Or Accessories
Mts Equipment Ground | Test Point 2 Ground Rod | 8.2 V | Same As Mts Equipment | Same As Mts Equipment | Same As Mts Equipment | Same As Mts Equipment
Genset | Test Point 3 Bare Copper Wire | NA | Connected To Grounding Busbar Of Mts | Same As Mts Equipment | (1) Unwanted Voltage Maybe Present On Non-Current Carrying Metal Objects | (1) Incorrect Operation Of Overcurrent Device With Ground Fault Protection
[5 empty] | (2) Equipment Might Be Damaged During A Fault Condition | (2) Health And Safety Risks For Facilities And Personnel

## CHE-Systemdesign
Risk CAT. | Range of calculated | Minimum Ppe Rating | Clothing Required
| incident energy [cal/$cm^2] | [Cal/Cm2]
0 | 0 < E $\leq$1.2 | N/A | 4.5-14.0 Oz/Yd2Untreated Cotton
1 | 1.2 < E $\leq$ 4 | 4 | Flame Retardant (Fr) Shirt And Pants
2 | 4 < E $\leq$ 8 | 8 | Cotton Underclothing Plus Fr Shirt And Pants
3 | 8 < E $\leq$ 25 | 25 | Cotton Underclothing Plus Fr Shirt, Pants, Overalls Or Equivalent
4 | 25 < E $\leq$40 | 40 | Cotton Underclothing Plus Fr Shirt, Pants, Plus Double Layer Switching Coat And Pants Or Equivalent
5 | 40 < E $\leq$ 100 | 100 | Cotton Underclothing Plus Fr Shirt, Pants, Plus Multi-Layer Switching Suit Or Equivalent
Protective Device Settings - Low Voltage Circuit Breaker with Thermal-Magnetic Trip Device
LVCB ID | Manufacturer | Breaker |  | Thermal |  | Magnetic (Inst.)
|  | Model | Size | Setting | Trip | Setting | Trip
[5 empty] | (Amps) |  | (Amps)
CB4 | Fuji Electric | BW400EAG | 250 | Fixed | 250 | Fixed | 8 xIn
CB9 | Fuji Electric | BW125JAG | 100 | Fixed | 100 | Fixed | 8 xIn
CB10 | Fuji Electric | BW125JAG | 100 | Fixed | 100 | Fixed | 8 xIn
CB11 | Fuji Electric | BW32SAG | 32 | Fixed | 32 | Fixed | 8 xIn
CB12 | Fuji Electric | BW32SAG | 32 | Fixed | 32 | Fixed | 8 xIn
CB1 | Fuji Electric | BW400EAG | 250 | Fixed | 250 | Fixed | 8 xIn
VOLTAGE DROP SUMMARY
Item | From | To | Wire Size, Mm² | I | Length Meters | R $\Omega$/305M | X $\Omega$/305M | Vd | \%Vd | Remarks
1 | Pole Mounted Transformer 50Kva,3$\Phi$ | Ats Panel | 250 | 425 | 15.52 | 0.048 | 0.027 | 2.06 | 0.43 | Within Limts | 43
2 | Mts Panel | Ecb 250A | 250 | 425 | 7 | 0.048 | 0.027 | 0.929 | 0.19 | Within Limts | 19
3 | Ecb 30A, 2P | Dry Type Transformer 2.5Kva | 5.5 | 40 | 4.2 | 1.2 | 0.063 | 1.324 | 0.55 | Within Limts | 55
4 | Dry Type Transformer 2.5Kva, 1$\Phi$ | Ups Panel | 5.5 | 40 | 4 | 1.2 | 0.063 | 1.261 | 0.53 | Within Limts | 53
5 | Mccb 100A, 3P | 30Hp Motor | 30 | 115 | 10 | 0.2 | 0.057 | 1.357 | 0.28 | Within Limts | 28
| Pole Mounted To 30 Hp Motor | [6 empty] | 3.417 | 0.71 | Within Limits | 71

## CHE-FDAS
Item | Visual Check | Status | Remarks
1 | Evacuation Plan | 0
2 | Fire Extinguishers | 0 | Pump Station Is Not Equipped With All Of The Standard Safety Features And Equipment
3 | Fire Exits | 0
4 | Fire Hose Cabinet | 0
5 | Fire Sprinkler System | 0
6 | Emergency Exit Signages | 0
7 | Emergency Lights | 0
8 | PPE Cabinet | 0
Item | Description | Status | Findings During Inspection | Remarks
1 | Rusty Hinge On Door | 0 | -Broken Hinge Of The Door | -Unsafe
-Door Will Not Be Aligned And Hard To Close
- Small Animals May Get Inside
2 | Unmaintained Door | 0 | -Rusty Door Opening | -Unsafe
|  |  | - Room Not Secure | -Operator Is Staying Inside The Room
|  |  | -Evidence Of Not Observing Cleanliness | -Unclean Environment
3 | Ladder | 0 | - Unprotected Ladder Going To Reservoir | -Unsafe
|  |  | -Tree Leaves Blocking The Ladder | -People Climbing Should Be Protected By Cage When Climbing
-Leaves Can Retain Water Adding To Slippage
4 | Outdoor Stairs | 0 | - No Hand Rail | -Unsafe
-Possible Slipping Of Operator When Going Up The Steps Specially After Rain Pour Or When There Is Drizzle
5 | Water Inside | 0 | - Water Ponding Inside The Structure | -Unsafe
| Struture |  |  | -Water Can Be Breeding For Mosquitos If Not Drained
6 | Defective Lighting | 0 | -Lighting Fixture Is Without Bulb (Not Functioning) | -Unsafe
| Fixture |  |  | - Can Be A Source Of Fire When Ignited And Not Stored Properly.
-Room Where The Operator Stays Is Not Well Lit During The Night
7 | Old Structure | 0 | - Room Was Disorganized With A Lot Of Materials And Devices Stored Inside The Room Where The Operator Stays. | -Unsafe
- Can Be A Source Of Fire When Ignited And Not Sored Properly.
8 | Hanging Wires | 0 | - Wires From The Room Were Not Harnessed Or Inside Conduit | -Unsafe
- Exposed Wires Still With Power And Can Be A Source Of Fire Hazard.
9 | Hanging Wires | 0 | - Wires From The Room Were Not Harnessed Or Inside Conduit. | -Unsafe
|  |  | -Visible Deterioration Of Wires | - Exposed Wires Are Still With Power And Can Be A Source Of Fire Hazard.
10 | Hanging Wires | 0 | - Wires From The Room Were Not Harnessed Or Inside Conduit | -Unsafe
|  |  | -Visible Deterioration Of Wire Insulation | - Still With Power And Can Be A Source Electrocution And Of Fire Hazard.