## R1P-BOQ
No. | Description | Items | CAT | CS | IT | Unit Cost | Quan. | Unit | Total | Remarks
1 | Pipe system | Modification of suction piping | P | 2 | 5 | 300000 | 1 | lot | 300000 | New suction line with option for long radius elbow and additional provision for straight pipe to facilitate more developed flow profile(See conceptual design)
2 | Pipe system | Replace pipe/refurbish heavily detriorated pipes | P | 2 | 1 | 250000 | 1 | lot | 250000 | Pipe replacement or restoration: extensive rust removal and recoating of pipes, new material for pressure reducing valve handle to avoid galvanic corrosion
3 | Pipe system | Addition of straight coupling along discharge side | P | 2 | 6 | 250000 | 1 | lot | 250000 | Provide a coupling for pipe internal inspection. Useful for determining extent of pipe scaling although quite a tedious task (see conceptual design)
4 | Instrumentation and Monitoring | Installation of pressure gauge near pump flange | M | 2 | 6 | 10000 | 6 | pc | 60000 | For increased accuracy in measuring head
5 | Instrumentation and Monitoring | Installation of UFM for Pumps 3 and 2 | M | 2 | 6 | 120000 | 2 | pc | 240000 | Basic simulation show flow is relatively develop and flow meters can gain confident measurements
6 | Instrumentation and Monitoring | Addition/upgrade to Key Software modules | M | 2 | 5 | 100000 | 1 | lot | 100000 | Will log average pump efficiency, individual and total production volumes (as determined by thermodynamic device), pump energy usage and real time pump curve data
7 | Instrumentation and Monitoring | Upgrade to vibration analyzer | M | 2 | 5 | 100000 | 1 | lot | 100000 | Will provide continuous monitoring of pump vibration activity and generate time based graphs of FFT and 3D spectrum
8 | Pump efficiency | Replacement of existing wear rings with non metallic wear rings | M | 2 | 5 | 150000 | 6 | pc | 900000 | Clearance can be reduced to up to 50% which in turn can lead up to 5% efficiency gain
9 | Lighting | lights under over sidewalk overhang | F | 2 | 5 | 5000 | 3 | pc | 15000 | For convenience rather than carrying portable lights
10 | Instrumentation and Monitoring | Control panel check-up | E | 2 | 1 | - | - | - | - | Check up to resolve minor nuisances such as units, readings and displays
11 | Reservoir | Check up and reinforment of reservoir walls | S | 2 | 1 | - | - | - | - | Walls were continued for height extension of reservoir however cracks were observed on the merging portion of the extension
12 | Pump efficiency | Anti-friction coatng | M | - | 5 | 100000 | 8 | pcs | 800000 | Further increases efficiency
14 | Lubrication method | Upgrade to automatic lubricators (eg. Single point lubricant dispensers) | M | - | 5 | 30000 | 6 | pcs | 180000 | Avoids under and over-lubrication problems
15 | Condition Monitoring | Regular Vibration Analysis | M | 2 | 7 | 3000 | - | per point | 160000 | To improve data pool and help closely monitor mechanical health via vibration analysis. (Price computed is based on perpetual basis of 15% rate)
| Total | [7 empty] | 3355000