## R1P_VISUAL
Item |  | Description | Model | Brand | Status |  | REMARKS
1 | Main Switch/Switchboard |  | MDP 460V/MDP230V | Local Fabrication | 1 | Functioning
2 | Distribution Transformer |  | 5kVA, 460V/230 | Mega Masterlink | 1 | Functioning
| Distribution Transformer |  | 15kVA, 460V/230 | Mega Masterlink | 1 | Functioning
| Distribution Transformer |  | 50kVA, 460V/230 | Mega Masterlink | 1 | Functioning
3 | Maynilad Owned Load Break Switch (LBS) |  | n/a | N/a | 0 | Low voltage installation
4 | Power Cables (secondary side of DT to the Elect. Loads) |  | THHN cables |  | 1
5 | Motor Control Center |  | 230V and 460V MCC | Local Assembly | 1 | Complete with nameplates
6 | Capacitor Bank |  | 225 kVAR | Local Assembly | 1 | Functioning
7 | TVSS |  | n/a | N/a | 0 | Not found
8 | Power Meter |  | Digital | Siemens Sentron | 1 | Functioning
9 | Filters and Reactors |  | 125HP 460V 3ph | Danfoss | 1 | Functioning
10 | Instrument Transformers |  | Current and Voltage |  | 1 | wiring acceptable
11 | Electrical Protective Relays |  | n/a | n/a | 0 | Not found
12 | Motor and Switches |  | Induction Motor | Teral | 1 | Functioning
13 | Transfer Switch |  | Automatic | Gensys Controller | 1 | Functioning
14 | Uninterruptible Power System (UPS) |  | Verify capacity | GE | 1 | Functioning
15 | Distrbution Panelboards and assoc. appurtenances |  | DP and LPB | locally fabricated | 1 | Breakers are Schneider brand
16 | Ground-Fault Circuit Interrupter (GFCI) or ELCB or (RCD) |  | n/a | n/a | 0 | Not found
17 | Lighting and Lighting Control System |  | Verify wattage | Fixture w/ Diffuser | 1 | Functioning fixtures
18 | Emergency Generator |  | Standby Genset | Cumper | 1 | Well maintained
19 | Building Service and Distribution |  | utility owned | 3 x 250kVA | 1 | Y-Y conection

## R1P_IR
| Location | Ayala Alabang R1P Pump Station
| Area served | MCC Room
| Instrument Used | Digital Insulation Resistance Tester, Calibtation Cert. No CRACL-1808-124
No. | Description | Voltage | Connectivity | [5 empty] | Remarks
|  | Voltage | L1-L2 | L2-L3 | L3-L1 | L1-G | L2-G | L3-G
1 | Normal Side Incoming power cable from ECB 1250AT outdoor to noraml ACB from ECB 1250AT outdoor to noraml ACB | 1kV | >2000 | >2000 | >2000 | 1423 | 1358 | 1179 | Within limits
2 | Emergency side incoming power cable from genset breaker to ATS emergency ACB | 1kV | 868 | 930 | 1044 | 518 | 530 | 531 | Within limits
3 | Common load busbar of ATS 1250AT to lineside of sub-main MCCB 1250AT | 1kV | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | Within limits
4 | Common main busbar of MCC | 1kV | >2000 | >2000 | >2000 | >2000 | >2000 | >2000 | Within limits

## R1P_safety2
Figure: Electrical Safety
ITEM | DESCRIPTION | STATUS | Findings During Inspection |  | Remarks
1 | Emergency lights | 0 | Most of the emergency lights has no | Should be checked for functionality
|  |  | inspection tag | Replace if no longer charging
2 | Ladder going to reservoir | 0 | Unprotected ladder | Unsafe for personnel going up the reservoir
|  |  | No cage | Cage should be provided for protection from fall
3 | Manhole#1 | 0 | Open manhole w/o barricade and | -Unsafe if unnoticed
|  |  | without signage | Should have barricade and signage for warning
4 | Manhole #2 | 0 | Open manhole w/ barricade but | Unsafe if unnoticed
|  |  | with signage | Should have signage to warn peolple at
a distance
5 | Fire Extinguisher | 0 | Last inspection tag 10/4/2017 | For FEX, this should be inspected once a month
Make sure this is still effective
6 | Fire Extinguisher | 0 | No FEX on designated location | For accessibility, FEX should be located in its
designated location

## R1P_safety1
Table: Electrical safety data highlights
ITEM | VISUAL CHECK | STATUS |  | REMARKS
1 | EVACUATION PLAN | 1 | Posted
2 | FIRE EXTINGUISHERS | 1 | Green FEX(HCFC) and Red FEX dry chemical
3 | FIRE EXITS | 1 | All doors have exit signages
4 | FIRE HOSE CABINET | 0 | Not found
5 | FIRE SPRINKLER SYSTEM | 0 | No sprinkler system
6 | EMERGENCY EXIT SIGNAGES | 1 | Found in every door
7 | EMERGENCY LIGHTS | 1 | Emergency lights are functioning (Aglow)
Mosy has no inspection tag
8 | PPE CABINET | 0 | Not found

## R1P_safety3
Table : Basis of Design
ITEM | DRAWINGS | STATUS |  | REMARKS
1 | Existing As-built drawings for FDAS | 1 | As built not found. Drawings for FDAS will be provided
2 | Existing As-built drawings for Emergency light location | 1 | As built not found. Drawings for FDAS will be provided
3 | Existing As-built for Fire Extinguisher location | 1 | As built not found. Drawings for FDAS will be provided

## R1P_fdas inspection
Table 1. | HIGHLIGHTS OF VISUAL INSPECTION OF FIRE DETECTION AND ALARM SYSTEM
No. | Assets | STATUS | REMARKS
A. | VISUAL CHECK OF FIRE ALARM CONTROL PANEL
1 | Panel Status, installed and location area | 1 | INSTALLED, LOCATED AT ENTRANCE
2 | Power indicator lamp operational | 1
3 | Devices properly indicated and marked | 1
4 | Panel clear from trouble indicators | 1
5 | Lamp test indicator operational | 1
6 | Zones properly indicated and marked | 1
7 | Check if it’s connected to sprinkler system | 0 | NO SPRINKLER INSTALLED AT SITE
B. | CHECKING OF INSTALLED DEVICES
1 | Check floor plan lay-out and location of the device if accessible/easy to access | 0 | No floor Plan presented during inspection
2 | Heat detectors and / or smoke detectors locations acceptable | 1
3 | Heat detectors and / or smoke detectors indicator lamp functioning | 1
4 | Pull station locations acceptable | 1
5 | Bells and buzzers operated correctly |  | FOR VERIFICATION
6 | Bells and buzzers audibility |  | FOR VERIFICATION
7 | Strobe lights locations are acceptable | 0 | NO STROBE LIGHT DEVICE
8 | Strobe light operated correctly | 0 | NO DEVICE
9 | Are Fire alarm zones (areas) clearly marked | 1
10 | Is there a maintenance and service contract for the fire alarm system | 1 | INFORMATION SUPPLIED BY OPERATOR AT SITE
11 | Does the Fire Alarm System smoke detector, heat detector, manual call point , horn and strobe light working and have a current inspection tag | 0 | NO INSPECTION TAG
12 | Is the fire alarm system in full working order |  | FOR VERIFICATION

## R!P_grounding
GROUNDING RESISTANCE MEASUREMENT TEST
SUMMARY OF FINDNGS
LOCATION | EQUIPMENT NAME /ROOM | MEASURED GROUNDING RESISTANCE | FINDINGS | RECCOMMENDATIONS | EFFECTS | RISKS
[5 empty] | IF NOT CORRECTED | (POSSIBLE OUTCOME)
LIGHTNING ARRESTER | TEST POINT 1 BARE COPPER WIRE | 2.99$\Omega$ | (1) Within the 5 ohms limit as per NFPA and IEE standards; | (1) Checking and retightening of loose grounding terminal connections; | Overheating on conductors and possible nuisance tripping of ground fault protection or relays | Damage to equipment or accessories
|  |  | (2) However, values are already within the marginal level of acceptability | (2) Replacement of corroded copper wires improper lugs for grounding terminations
LIGHTNING ARRESTER | TEST POINT 1 GROUND ROD | 2.97$\Omega$ | (1) Within the 5 ohms limit as per NFPA and IEE standards; | (1) Checking and retightening of loose grounding terminal connections | (1) Overheating on conductors and possible nuisance tripping of ground fault protection or relays | Damage to equipment or accessories
|  |  | (2) However, values are already within the marginal level of acceptability | (2) Replacement of corroded copper wires improper lugs for grounding terminations
NEAR LVSG/MOTOR CONTROL CENTER | TEST POINT 2 COPPER WIRE | 0.31$\Omega$ | Within the 5 ohms limit as per NFPA and IEE standards | None | None | None
NEAR LVSG/MOTOR CONTROL CENTER | TEST POINT 1 GROUND ROD | 0.31$\Omega$ | Within the 5 ohms limit as per NFPA and IEE standards | None | None | None