## R1P_VISUAL
Item |  | Description | Model | Brand | Status |  | REMARKS
1 | Main Switch/Switchboard |  | MDP 460V/MDP230V | Local Fabrication | 1 | Functioning
2 | Distribution Transformer |  | 5kVA, 460V/230 | Mega Masterlink | 1 | Functioning
| Distribution Transformer |  | 15kVA, 460V/230 | Mega Masterlink | 1 | Functioning
| Distribution Transformer |  | 50kVA, 460V/230 | Mega Masterlink | 1 | Functioning
3 | Maynilad Owned Load Break Switch (LBS) |  | n/a | N/a | 0 | Low voltage installation
4 | Power Cables (secondary side of DT to the Elect. Loads) |  | THHN cables |  | 1
5 | Motor Control Center |  | 230V and 460V MCC | Local Assembly | 1 | Complete with nameplates
6 | Capacitor Bank |  | 225 kVAR | Local Assembly | 1 | Functioning
7 | TVSS |  | n/a | N/a | 0 | Not found
8 | Power Meter |  | Digital | Siemens Sentron | 1 | Functioning
9 | Filters and Reactors |  | 125HP 460V 3ph | Danfoss | 1 | Functioning
10 | Instrument Transformers |  | Current and Voltage |  | 1 | wiring acceptable
11 | Electrical Protective Relays |  | n/a | n/a | 0 | Not found
12 | Motor and Switches |  | Induction Motor | Teral | 1 | Functioning
13 | Transfer Switch |  | Automatic | Gensys Controller | 1 | Functioning
14 | Uninterruptible Power System (UPS) |  | Verify capacity | GE | 1 | Functioning
15 | Distrbution Panelboards and assoc. appurtenances |  | DP and LPB | locally fabricated | 1 | Breakers are Schneider brand
16 | Ground-Fault Circuit Interrupter (GFCI) or ELCB or (RCD) |  | n/a | n/a | 0 | Not found
17 | Lighting and Lighting Control System |  | Verify wattage | Fixture w/ Diffuser | 1 | Functioning fixtures
18 | Emergency Generator |  | Standby Genset | Cumper | 1 | Well maintained
19 | Building Service and Distribution |  | utility owned | 3 x 250kVA | 1 | Y-Y conection

## R1P_IR
Location | Ayala Alabang R1P Pump Station
Area served | MCC Room
Instrument Used | Digital Insulation Resistance Tester, Calibtation Cert. No CRACL-1808-124
Description | Test Voltage | L1-L2 | L2-L3 | L3-L1 | L1-G | L2-G | L3-G | REMARKS
Normal Side Incoming power cable | 1kV | >2000 MΩ | >2000 MΩ | >2000 MΩ | 1423 MΩ | 1358 MΩ | 1179 MΩ | Within
from ECB 1250AT outdoor to noraml ACB | [7 empty] | limits
Emergency side incoming power cable | 1kV | 868MΩ | 930MΩ | 1044MΩ | 518MΩ | 530MΩ | 531MΩ | Within
from genset breaker to ATS emergency ACB | [7 empty] | limits
Common load busbar of ATS 1250AT to | 1kV | >2000 MΩ | >2000 MΩ | >2000 MΩ | >2000 MΩ | >2000 MΩ | >2000 MΩ | Within
lineside of sub-main MCCB 1250AT | [7 empty] | limits
Common main busbar of MCC | 1kV | >2000 MΩ | >2000 MΩ | >2000 MΩ | >2000 MΩ | >2000 MΩ | >2000 MΩ | Within
limits

## R1P_safety2
Figure: Electrical Safety
Item | Description | Status | Findings | Remarks
1 | Emergency lights | 0 | Most of the emergency lights has no inspection tag | Should be checked for functionality
Replace if no longer charging
2 | Ladder going to reservoir | 0 | Unprotected ladder | Unsafe for personnel going up the reservoir
|  |  | No cage | Cage should be provided for protection from fall
3 | Manhole#1 | 0 | Open manhole w/o barricade and | -Unsafe if unnoticed
|  |  | without signage | Should have barricade and signage for warning
4 | Manhole #2 | 0 | Open manhole w/ barricade but | Unsafe if unnoticed
|  |  | with signage | Should have signage to warn peolple at a distance
5 | Fire Extinguisher | 0 | Last inspection tag 10/4/2017 | For FEX, this should be inspected once a month
Make sure this is still effective
6 | Fire Extinguisher | 0 | No FEX on designated location | For accessibility, FEX should be located in its
designated location

## R1P_safety1
Table: Electrical safety data highlights
Items | Visual inspection on | Status | Remarks
1 | Evacuation Plan | 1 | Posted | EVACUATION PLAN
2 | Fire Extinguishers | 1 | Green FEX(HCFC) and Red FEX dry chemical | FIRE EXTINGUISHERS
3 | Fire Exits | 1 | All doors have exit signages | FIRE EXITS
4 | Fire Hose Cabinet | 0 | Not found | FIRE HOSE CABINET
5 | Fire Sprinkler System | 0 | No sprinkler system | FIRE SPRINKLER SYSTEM
6 | Emergency Exit Signages | 1 | Found in every door | EMERGENCY EXIT SIGNAGES
7 | Emergency Lights | 1 | Emergency lights are functioning (Aglow) Mosy has no inspection tag | EMERGENCY LIGHTS
8 | Ppe Cabinet | 0 | Not found | PPE CABINET

## R1P_safety3
Table : Basis of Design
ITEM | DRAWINGS | STATUS |  | REMARKS
1 | Existing As-built drawings for FDAS | 1 | As built not found. Drawings for FDAS will be provided
2 | Existing As-built drawings for Emergency light location | 1 | As built not found. Drawings for FDAS will be provided
3 | Existing As-built for Fire Extinguisher location | 1 | As built not found. Drawings for FDAS will be provided

## R1P_fdas inspection
Table 1. | HIGHLIGHTS OF VISUAL INSPECTION OF FIRE DETECTION AND ALARM SYSTEM
No. | Assets | STATUS | REMARKS
A. | VISUAL CHECK OF FIRE ALARM CONTROL PANEL
1 | Panel Status, installed and location area | 1 | INSTALLED, LOCATED AT ENTRANCE
2 | Power indicator lamp operational | 1
3 | Devices properly indicated and marked | 1
4 | Panel clear from trouble indicators | 1
5 | Lamp test indicator operational | 1
6 | Zones properly indicated and marked | 1
7 | Check if it’s connected to sprinkler system | 0 | NO SPRINKLER INSTALLED AT SITE
B. | CHECKING OF INSTALLED DEVICES
1 | Check floor plan lay-out and location of the device if accessible/easy to access | 0 | No floor Plan presented during inspection
2 | Heat detectors and / or smoke detectors locations acceptable | 1
3 | Heat detectors and / or smoke detectors indicator lamp functioning | 1
4 | Pull station locations acceptable | 1
5 | Bells and buzzers operated correctly |  | FOR VERIFICATION
6 | Bells and buzzers audibility |  | FOR VERIFICATION
7 | Strobe lights locations are acceptable | 0 | NO STROBE LIGHT DEVICE
8 | Strobe light operated correctly | 0 | NO DEVICE
9 | Are Fire alarm zones (areas) clearly marked | 1
10 | Is there a maintenance and service contract for the fire alarm system | 1 | INFORMATION SUPPLIED BY OPERATOR AT SITE
11 | Does the Fire Alarm System smoke detector, heat detector, manual call point , horn and strobe light working and have a current inspection tag | 0 | NO INSPECTION TAG
12 | Is the fire alarm system in full working order |  | FOR VERIFICATION