## R1P_VISUAL
Item | Description | Model | Brand | Status | Remarks
1 | Main Switch/Switchboard | MDP 460V/MDP230V | Local Fabrication | 1 | Functioning
2 | Distribution Transformer | 5kVA, 460V/230 | Mega Masterlink | 1 | Functioning
3 | Distribution Transformer | 15kVA, 460V/230 | Mega Masterlink | 1 | Functioning
4 | Distribution Transformer | 50kVA, 460V/230 | Mega Masterlink | 1 | Functioning
5 | Maynilad Owned Load Break Switch (LBS) | n/a | N/a | 0 | Low voltage installation
6 | Power Cables (secondary side of DT to the Elect. Loads) | THHN cables |  | 1
7 | Motor Control Center | 230V and 460V MCC | Local Assembly | 1 | Complete with nameplates
8 | Capacitor Bank | 225 kVAR | Local Assembly | 1 | Functioning
9 | TVSS | n/a | N/a | 0 | Not found
10 | Power Meter | Digital | Siemens Sentron | 1 | Functioning
11 | Filters and Reactors | 125HP 460V 3ph | Danfoss | 1 | Functioning
12 | Instrument Transformers | Current and Voltage |  | 1 | wiring acceptable
13 | Electrical Protective Relays | n/a | n/a | 0 | Not found
14 | Motor and Switches | Induction Motor | Teral | 1 | Functioning
15 | Transfer Switch | Automatic | Gensys Controller | 1 | Functioning
16 | Uninterruptible Power System (UPS) | Verify capacity | GE | 1 | Functioning
17 | Distrbution Panelboards and assoc. appurtenances | DP and LPB | locally fabricated | 1 | Breakers are Schneider brand
18 | Ground-Fault Circuit Interrupter (GFCI) or ELCB or (RCD) | n/a | n/a | 0 | Not found
19 | Lighting and Lighting Control System | Verify wattage | Fixture w/ Diffuser | 1 | Functioning fixtures
20 | Emergency Generator | Standby Genset | Cumper | 1 | Well maintained
21 | Building Service and Distribution | utility owned | 3 x 250kVA | 1 | Y-Y conection

## R1P_short circuit
Item | Description | SCC (kA) | Kaic \& CB (kA) | REMARKS
1 | From Utility to tansformer | 13.633 | Utility owned trafo | Protection c/o Utility
2 | Pole Mounted transformer to main circuit breaker 1250A in pedestal | 13.633 | 65 | Existing is acceptable
3 | Main circuit breaker to Automatic transfer switch panel | 13.129 | 65 | Exsisting is acceptable
4 | Automatic transfer switch panel to MCC PANEL at control room | 13.094 | 65 | Existing acceptable
5 | 480V Bus to TVSS CB protection | 13.094 | 25 | Existing acceptable
6 | 480V Bus to Motor 1 CB protection | 13.094 | 35 | Existing acceptable
7 | 480V Bus to Motor 2 CB protection | 13.094 | 35 | Existing acceptable
8 | 480V Bus to Motor 3 CB protection | 13.094 | 35 | Existing acceptable
9 | 480V Bus to 10 HP Motor 3 CB protection | 13.094 | 25 | Existing acceptable
10 | 480V Bus to 10 HP Motor 3 CB protection | 13.094 | 25 | Existing acceptable
11 | 480V Bus to DP1 CB protection | 13.094 | 35 | Existing acceptable
12 | 480V Bus to 9.38kVA Motor CB protection | 13.094 | 25 | Existing acceptable
13 | 480V Bus to FTPP PANEL CB protection | 13.094 | 25 | Existing acceptable
14 | 480V Bus to 5kVA transformer CB protection | 13.094 | 25 | Existing acceptable
15 | Transformer to CAPP panel | 0.533 | 25 | Existing acceptable

## R1P_sc
ITEM NO. |  | DESCRIPTION | CALCULATED |  | AS FOUND |  |  | REMARKS
|  |  | SHORT CIRCUIT |  | EXISTING CB
1 | From Utility to tansformer |  | 13.633 | kA | Utility owned trafo |  | Protection c/o Utility
2 | Pole Mounted transformer to main |  | 13.633 | kA | 65 | kA | Existing is acceptable
circuit breaker 1250A in pedestal
3 | Main circuit breaker to |  | 13.129 | kA | 65 | kA | Exsisting is acceptable
Automatic transfer switch panel
4 | Automatic transfer switch panel to |  | 13.094 | kA | 65 | kA | Existing acceptable
MCC PANEL at control room
5 | 480V Bus to TVSS CB protection |  | 13.094 | kA | 25 | kA | Existing acceptable
6 | 480V Bus to Motor 1 CB protection |  | 13.094 | kA | 35 | kA | Existing acceptable
7 | 480V Bus to Motor 2 CB protection |  | 13.094 | kA | 35 | kA | Existing acceptable
8 | 480V Bus to Motor 3 CB protection |  | 13.094 | kA | 35 | kA | Existing acceptable
9 | 480V Bus to 10 HP Motor 3 CB protection |  | 13.094 | kA | 25 | kA | Existing acceptable
10 | 480V Bus to 10 HP Motor 3 CB protection |  | 13.094 | kA | 25 | kA | Existing acceptable
11 | 480V Bus to DP1 CB protection |  | 13.094 | kA | 35 | kA | Existing acceptable
12 | 480V Bus to 9.38kVA Motor CB protection |  | 13.094 | kA | 25 | kA | Existing acceptable
13 | 480V Bus to FTPP PANEL CB protection |  | 13.094 | kA | 25 | kA | Existing acceptable
14 | 480V Bus to 5kVA transformer CB |  | 13.094 | kA | 25 | kA | Existing acceptable
protection
15 | Transformer to CAPP panel |  | 0.533 | kA | 25 | kA | Existing acceptable

## R1P_IR
Location | Ayala Alabang R1P Pump Station
Area served | MCC Room
Instrument Used | Digital Insulation Resistance Tester, Calibtation Cert. No CRACL-1808-124
Description | Test Voltage | L1-L2 | L2-L3 | L3-L1 | L1-G | L2-G | L3-G | REMARKS
Normal Side Incoming power cable | 1kV | >2000 MΩ | >2000 MΩ | >2000 MΩ | 1423 MΩ | 1358 MΩ | 1179 MΩ | Within
from ECB 1250AT outdoor to noraml ACB | [7 empty] | limits
Emergency side incoming power cable | 1kV | 868MΩ | 930MΩ | 1044MΩ | 518MΩ | 530MΩ | 531MΩ | Within
from genset breaker to ATS emergency ACB | [7 empty] | limits
Common load busbar of ATS 1250AT to | 1kV | >2000 MΩ | >2000 MΩ | >2000 MΩ | >2000 MΩ | >2000 MΩ | >2000 MΩ | Within
lineside of sub-main MCCB 1250AT | [7 empty] | limits
Common main busbar of MCC | 1kV | >2000 MΩ | >2000 MΩ | >2000 MΩ | >2000 MΩ | >2000 MΩ | >2000 MΩ | Within
limits

## R1P_safety2
Figure: Electrical Safety
ITEM | DESCRIPTION | STATUS | Findings During Inspection |  | Remarks
1 | Emergency lights | 0 | Most of the emergency lights has no | Should be checked for functionality
|  |  | inspection tag | Replace if no longer charging
2 | Ladder going to reservoir | 0 | Unprotected ladder | Unsafe for personnel going up the reservoir
|  |  | No cage | Cage should be provided for protection from fall
3 | Manhole#1 | 0 | Open manhole w/o barricade and | -Unsafe if unnoticed
|  |  | without signage | Should have barricade and signage for warning
4 | Manhole #2 | 0 | Open manhole w/ barricade but | Unsafe if unnoticed
|  |  | with signage | Should have signage to warn peolple at
a distance
5 | Fire Extinguisher | 0 | Last inspection tag 10/4/2017 | For FEX, this should be inspected once a month
Make sure this is still effective
6 | Fire Extinguisher | 0 | No FEX on designated location | For accessibility, FEX should be located in its
designated location

## R1P_safety1
Table: Electrical safety data highlights
ITEM | VISUAL CHECK | STATUS |  | REMARKS
1 | EVACUATION PLAN | 1 | Posted
2 | FIRE EXTINGUISHERS | 1 | Green FEX(HCFC) and Red FEX dry chemical
3 | FIRE EXITS | 1 | All doors have exit signages
4 | FIRE HOSE CABINET | 0 | Not found
5 | FIRE SPRINKLER SYSTEM | 0 | No sprinkler system
6 | EMERGENCY EXIT SIGNAGES | 1 | Found in every door
7 | EMERGENCY LIGHTS | 1 | Emergency lights are functioning (Aglow)
Mosy has no inspection tag
8 | PPE CABINET | 0 | Not found

## R1P_safety3
Table : Basis of Design
ITEM | DRAWINGS | STATUS |  | REMARKS
1 | Existing As-built drawings for FDAS | 1 | As built not found. Drawings for FDAS will be provided
2 | Existing As-built drawings for Emergency light location | 1 | As built not found. Drawings for FDAS will be provided
3 | Existing As-built for Fire Extinguisher location | 1 | As built not found. Drawings for FDAS will be provided

## R1P_fdas inspection
Table 1. | HIGHLIGHTS OF VISUAL INSPECTION OF FIRE DETECTION AND ALARM SYSTEM
No. | Assets | STATUS | REMARKS
A. | VISUAL CHECK OF FIRE ALARM CONTROL PANEL
1 | Panel Status, installed and location area | 1 | INSTALLED, LOCATED AT ENTRANCE
2 | Power indicator lamp operational | 1
3 | Devices properly indicated and marked | 1
4 | Panel clear from trouble indicators | 1
5 | Lamp test indicator operational | 1
6 | Zones properly indicated and marked | 1
7 | Check if it’s connected to sprinkler system | 0 | NO SPRINKLER INSTALLED AT SITE
B. | CHECKING OF INSTALLED DEVICES
1 | Check floor plan lay-out and location of the device if accessible/easy to access | 0 | No floor Plan presented during inspection
2 | Heat detectors and / or smoke detectors locations acceptable | 1
3 | Heat detectors and / or smoke detectors indicator lamp functioning | 1
4 | Pull station locations acceptable | 1
5 | Bells and buzzers operated correctly |  | FOR VERIFICATION
6 | Bells and buzzers audibility |  | FOR VERIFICATION
7 | Strobe lights locations are acceptable | 0 | NO STROBE LIGHT DEVICE
8 | Strobe light operated correctly | 0 | NO DEVICE
9 | Are Fire alarm zones (areas) clearly marked | 1
10 | Is there a maintenance and service contract for the fire alarm system | 1 | INFORMATION SUPPLIED BY OPERATOR AT SITE
11 | Does the Fire Alarm System smoke detector, heat detector, manual call point , horn and strobe light working and have a current inspection tag | 0 | NO INSPECTION TAG
12 | Is the fire alarm system in full working order |  | FOR VERIFICATION

## R!P_grounding
GROUNDING RESISTANCE MEASUREMENT TEST
SUMMARY OF FINDNGS
LOCATION | EQUIPMENT NAME /ROOM | MEASURED GROUNDING RESISTANCE | FINDINGS | RECCOMMENDATIONS | EFFECTS | RISKS
[5 empty] | IF NOT CORRECTED | (POSSIBLE OUTCOME)
LIGHTNING ARRESTER | TEST POINT 1 BARE COPPER WIRE | 2.99Ω | (1) Within the 5 ohms limit as per NFPA and IEE standards (2) However, values are already within the marginal level of acceptability | (1) Checking and retightening of loose grounding terminal connections (2) Replacement of corroded copper wires improper lugs for grounding terminations | (1) Overheating on conductors and possible nuisance tripping of ground fault protection or relays | Damage to equipment or accessories
LIGHTNING ARRESTER | TEST POINT 1 GROUND ROD | 2.97Ω | (1) Within the 5 ohms limit as per NFPA and IEE standards (2) However, values are already within the marginal level of acceptability | (1) Checking and retightening of loose grounding terminal connections (2) Replacement of corroded copper wires improper lugs for grounding terminations | (1) Overheating on conductors and possible nuisance tripping of ground fault protection or relays | Damage to equipment or accessories
NEAR LVSG/MOTOR CONTROL CENTER | TEST POINT 2 COPPER WIRE | 0.31Ω | Within the 5 ohms limit as per NFPA and IEE standards | None | None | None
NEAR LVSG/MOTOR CONTROL CENTER | TEST POINT 1 GROUND ROD | 0.31Ω | Within the 5 ohms limit as per NFPA and IEE standards | None | None | None

## R1P_rms voltage
Table 1.14 RMS Voltage Compliance
RMS VOLTAGE (480 VOLTS) | PHASE | MINIMUM | AVERAGE | MAXIMUM | LIMITS | REMARKS
MAIN ATS 1250A | AB | 457.6 | 476.6 | 482.56
(Load Side) | BC | 459.74 | 482.8 | 488.64 | ±10% (432-528V) | WITHIN LIMITS
| CA | 457.6 | 476.6 | 482.56
| AB | 451.46 | 474.8 | 487.3
VFD-1 | BC | 459.94 | 482.6 | 494 | ±10% (432-528V) | WITHIN LIMITS
| CA | 451.46 | 474.8 | 487.3
| AB | 456.02 | 477.7 | 483.02
VFD-2 | BC | 464.3 | 484.2 | 489.02 | ±10% (432-528V) | WITHIN LIMITS
| CA | 456.02 | 477.7 | 483.02
| AB | 459.2 | 476.1 | 481.38
Softstarter | BC | 465.4 | 482.7 | 487.58 | ±10% (432-528V) | WITHIN LIMITS
| CA | 459.2 | 476.1 | 481.38

## R1p_voltage drop
VOLTAGE DROP SUMMARY COMPUTATION
AYALA ALABANG R1P PUMP STATION
FEEDER CABLE VOLTAGE DROP
Item | From | To | Wire Size, mm² | I | Length Meters | R Ω/305m | X Ω/305m | VD | %VD | Remarks
1 | Transformer | Main circuit Breaker at 1250A pedestal | 4-200 | 360 | 15 | 0.035 | 0.049 | 0.4611 | 0.09606% | Within Limits | 0.00096062 | 0.096062
2 | Main circuit Breaker at 1250A pedestal | Automatic Transfer Switch 1250A | 4-200 | 360 | 21.14 | 0.035 | 0.049 | 0.64984 | 0.1354% | Within Limits | 0.0013538 | 0.13538
3 | Automatic Transfer Switch 1250A | MCC PANEL at control room | 4-200 | 360 | 1.5 | 0.035 | 0.049 | 0.04611 | 0.009606% | Within Limits | 9.6062e-05 | 0.0096062
4 | MCC PANEL at control room | Motor1, 120HP | 60 | 170 | 1.8 | 0.1 | 0.054 | 0.11402 | 0.02375% | Within Limits | 0.00023754 | 0.023754
5 | MCC PANEL at control room | Motor2, 120HP | 60 | 170 | 2.1 | 0.1 | 0.054 | 0.23013 | 0.04794% | Within Limits | 0.00047944 | 0.047944
6 | MCC PANEL at control room | Motor3, 120HP | 60 | 170 | 2.4 | 0.1 | 0.054 | 0.15203 | 0.03167% | Within Limits | 0.00031673 | 0.031673
7 | MCC PANEL at control room | DOL 10HP | 3.5 | 30 | 2.4 | 2 | 0.068 | 0.81726 | 0.1703% | Within Limits | 0.0017026 | 0.17026
8 | MCC PANEL at control room | DP1 PANELBOARD | 3.5 | 30 | 10 | 2 | 0.068 | 3.4052 | 0.7094% | Within Limits | 0.0070943 | 0.70943
9 | MCC PANEL at control room | Dry type trafo | 5.5 | 40 | 7.8 | 1.2 | 0.063 | 2.1266 | 0.443% | Within Limits | 0.0044304 | 0.44304
10 | MCC PANEL at control room | Capacitor bank 225 kVAR | 175 | 345 | 5.52 | 0.039 | 0.05 | 0.68497 | 0.1427% | Within Limits | 0.001427 | 0.1427

## R1P_voltage unbalance
Table 1.15 Voltage Unbalance Compliance
Voltage Unbalance | MINIMUM Deviation | AVERAGE Deviation | MAXIMUM Deviation | LIMITS (%) | REMARKS
MAIN (Load Side) | 0.31129 | 0.86351 | 0.83645 | ±2.5% | WITHIN LIMITS
VFD-1 | 1.2444 | 1.0892 | 0.91243 | ±2.5% | WITHIN LIMITS
VFD-2 | 1.2032 | 0.90303 | 0.82471 | ±2.5% | WITHIN LIMITS
Softstarter | 0.89608 | 0.91992 | 0.85497 | ±2.5% | WITHIN LIMITS

## R1P_current unbalance
Table 1.1 Current Unbalance Compliance
Current Unbalance | MINIMUM Deviation | AVERAGE Deviation | MAXIMUM Deviation | LIMITS (%) | REMARKS
MAIN ATS 1250A (Load Side) | 3.7416 | 5.837 | 2.0076 | ±10% | Within Limits
VFD-1 | 6.2699 | 6.1081 | 5.9869 | ±10% | Within Limits
VFD-2 | 3.6274 | 3.4608 | 3.6088 | ±10% | Within Limits
Softstarter | 5.9582 | 5.9567 | 1.1696 | ±10% | Within Limits

## R1P_THD
Table 1.18 Power Quality - Total Harmonic Distortion Compliance
TOTAL DEMAND DISTORTION (%) | PHASE | MINIMUM | AVERAGE | MAXIMUM | LIMITS (5%) | REMARKS
MAIN ATS 1250A | AB | 0.57 | 0.88 | 2.39
(Load Side) | BC | 0.62 | 0.91 | 2.32 | ≤ 5% | Within limits
| CA | 0.57 | 0.88 | 2.39
| AB | 0.45 | 0.89 | 2.39
VFD-1 | BC | 0.51 | 0.98 | 2.33 | ≤ 5% | Within limits
| CA | 0.45 | 0.89 | 2.39
| AB | 0.57 | 0.88 | 1.02
VFD-2 | BC | 0.61 | 0.96 | 2.27 | ≤ 5% | Within limits
| CA | 0.57 | 0.6 | 2.3
| AB | 0.59 | 0.92 | 2.3
Softstarter | BC | 0.69 | 0.95 | 2.24 | ≤ 5% | Within limits
| CA | 0.59 | 0.92 | 2.3

## R1P_TDD
Table 1.18 Power Quality - Total Demand Distortion Compliance
TOTAL DEMAND DISTORTION (%) | PHASE | MINIMUM | AVERAGE | MAXIMUM | LIMITS (5%) | REMARKS
MAIN ATS 1250A | AB | 1.28% | 4.89% | 26.82% |  |  | 1.28 | 4.89 | 26.82
(Load Side) | BC | 1.28% | 4.73% | 25.67% | ≤ 5% | Outside limits | 1.28 | 4.73 | 25.67
| CA | 1.37% | 4.71% | 25.98% |  |  | 1.37 | 4.71 | 25.98
| AB | 25.74% | 27% | 61.62% |  |  | 25.74 | 27 | 61.62
VFD-1 | BC | 24.9% | 25.9% | 55.23% | ≤ 5% | Outside limits | 24.9 | 25.9 | 55.23
| CA | 25.67% | 26.87% | 57.07% |  |  | 25.67 | 26.87 | 57.07
| AB | 24.24% | 25.01% | 37.14% |  |  | 24.24 | 25.01 | 37.14
VFD-2 | BC | 23.59% | 24.42% | 52.61% | ≤ 5% | Outside limits | 23.59 | 24.42 | 52.61
| CA | 23.78% | 24.62% | 72.75% |  |  | 23.78 | 24.62 | 72.75
| AB | 0.48% | 0.49% | 55.46% |  |  | 0.48 | 0.49 | 55.46
Softstarter | BC | 0.4% | 0.455% | 134.5% | ≤ 5% | Outside limits | 0.4 | 0.455 | 134.49
| CA | 0.44% | 0.48% | 52.65% |  |  | 0.44 | 0.48 | 52.65

## R1P_frequency
Table 1.19 Frequency Compliance
Frequency (Hz) | MINIMUM | AVERAGE | MAXIMUM | LIMITS | REMARKS
MAIN 1250A (Load Side) | 59.68 | 60.17 | 60.477 | 59.7-60.3 | Outside limits
VFD-1 | 59.744 | 60.07 | 60.34 | 59.7-60.3 | Within limits
VFD-2 | 59.66 | 60.12 | 60.364 | 59.7-60.3 | Outside limits
Softstarter | 59.59 | 60.22 | 60.439 | 59.7-60.3 | Outside limits

## R1P_power factor
Table 1.20 Power Factor Compliance
Power Factor | MINIMUM | AVERAGE | MAXIMUM | LIMITS (%) | REMARKS
MAIN ATS 1250A (Load Side) | 0.79 | 0.87 | 0.87 | >0.85% | WITHIN LIMITS
VFD-1 | 0.92 | 0.92 | 0.92 | >0.85% | Outside limits
VFD-2 | 0.93 | 0.93 | 0.93 | >0.85% | WITHIN LIMITS
Softstarter | 0.88 | 0.89 | 0.9 | >0.85% | WITHIN LIMITS

## R1P-crest factor
Table | Power Quality-Crest factor compliance
MAIN | VOLTAGE |  | CURRENT |  | Crest Factor – A high crest factor value for current was recorded to signify a distorted current waveform. A CF of 1.8 or higher means high waveform distortion.
Phase | MIN | MAX | MIN | MAX | distorted current waveform. A CF of 1.8 or higher means high waveform distortion.
A | 1.41 | 1.45 | 1.36 | 2.14
B | 1.41 | 1.46 | 1.36 | 2.08
C | 1.42 | 1.47 | 1.38 | 2.08
VFD-1 | VOLTAGE |  | CURRENT
Phase | MIN | MAX | MIN | MAX
A | 1.41 | 1.46 | 1.53 | 5.18
B | 1.41 | 1.62 | 1.62 | 6.29
C | 1.42 | 1.47 | 1.55 | 6.07
VFD-2 | VOLTAGE |  | CURRENT
Phase | MIN | MAX | MIN | MAX
A | 1.42 | 1.46 | 1.45 | 11.08
B | 1.41 | 1.45 | 1.51 | 8.39
C | 1.42 | 1.46 | 1.43 | 11.95
SS-3 | VOLTAGE |  | CURRENT
Phase | MIN | MAX | MIN | MAX
A | 1.41 | 1.48 | 1.37 | 5.15
B | 1.41 | 1.44 | 1.06 | 70.51
C | 1.42 | 1.48 | 1.27 | 4.73

## R1P_flicker
Table 1.21 Flicker Compliance
Flicker | Parameter | AB | BC | CA | LIMITS | REMARKS
MAIN ATS 1250A | Plt | 0.306 | 0.342 | 0.286 | ≤0.8 | Within Limits
(Load Side) | Pst | 0.593 | 0.713 | 0.55 | ≤1.0 | Within Limits
| Plt | 0.346 | 0.248 | 0.241 | ≤0.8 | Within Limits
VFD-1 | Pst | 0.755 | 0.51 | 0.521 | ≤1.0 | Within Limits
| Plt | 0.485 | 0.705 | 0.24 | ≤0.8 | Within Limits
VFD-2 | Pst | 0.972 | 1.356 | 0.51 | ≤1.0 | Within Limits
| Plt | 0.477 | 0.38 | 0.287 | ≤0.8 | Within Limits
Softstarter | Pst | 1.061 | 0.835 | 0.494 | ≤1.0 | Outside Limits