## RCM
Asset Code | Name | Station ID | Asset Description | Component | Failure Mode | Criticality | Failure Pattern | Task | Frequency | Done by | Comments
WSO-PAGPS-0022 | Storage Pump 1 | PAG | Horizontal pump between bearings | Bearings | Loss of lubrication | High | Age-related | Scheduled greasing | Weekly | Maintenance contractor | Avoid overgreasing. Use correct grease as stipulated by bearing manufacturer.
WSO-PAGPS-0022 | Storage Pump 1 | PAG | Horizontal pump between bearings | Bearings | High vibration due to cavitation | High | Random | Monitor suction pressure not to go below xx head. | Every hour | Operator | Refer to pump specifications on minimum NPSH requirements. Follow company policy in dealing with cavitation issues (e.g. call MCC to increase suction pressure and/or shutdown pumps)
WSO-PAGPS-0022 | Storage Pump 1 | PAG | Horizontal pump between bearings | Bearings | High vibration due to bearing failure (e.g. foreign materials in lubrication) | High | Random | Vibration monitoring | 2-weekly (every 2 weeks) | Maintenance contractor | Use trained contractor for the appropriate vibration monitoring device. Report findings every month.
WSO-PAGPS-0022 | Storage Pump 1 | PAG | Horizontal pump between bearings | Packing | Excessive leaks | Medium | Age-related | Tighten packing bolts | 2-weekly (every 2 weeks) | Maintenance contractor | Avoid overtightening of packing bolts.
WSO-PAGPS-0022 | Storage Pump 1 | PAG | Horizontal pump between bearings | Motor | Motor trip due to overloading | High | Random | Motor (skin) temperature measurement | Every hour | Operator | Refer to motor specifications on maximum allowable surface temperature.
WSO-PAGPS-0022 | Storage Pump 1 | PAG | Horizontal pump between bearings | Motor | Motor burns due to failure of winding insulation | Low | Age-related | Test/measure motor winding insulation | Annually | Maintenance contractor | Use qualified maintenance contractor.
WSO-PAGPS-0022 | Storage Pump 1 | PAG | Horizontal pump between bearings | Suction isolating valve | Valve passing (leaks) | Medium | Age-related | Test valve integrity | Annually | Maintenance contractor | Use qualified maintenance contractor. Failure of this valve may cause problems during maintenance of pump/motor.
WSO-PAGPS-0022 | Storage Pump 1 | PAG | Horizontal pump between bearings | Discharge isolating valve | Valve passing (leaks) | Low | Age-related | Test valve integrity | Annually | Maintenance contractor | Use qualified maintenance contractor. Failure of this valve is not critical as long as the check valve is working.
WSO-PAGPS-0022 | Storage Pump 1 | PAG | Horizontal pump between bearings | Pressure gauge (suction & discharge) | Pressure gauge reading is wrong due to wear | Low | Age-related | Replace pressure gauge | Annually | Maintenance contractor | Replace with calibrated pressure gauge. Mark with acceptable operating range. Criticality is low if the online pressure sensors are still functioning properly.
WSO-PAGPS-0022 | Storage Pump 1 | PAG | Horizontal pump between bearings | Pressure sensors (suction & discharge) | Pressure reading is erroneous | High | Random | Calibrate pressure sensors | Semi-annually (every 6 months) | Maintenance contractor | Use qualified maintenance contractor.
WSO-PAGPS-0022 | Storage Pump 1 | PAG | Horizontal pump between bearings | Flange | Leaks due to loose bolts and/or gasket failure | Medium | Age-related | Re-tighten bolts using specified torque values | Annually | Maintenance contractor | Use proper bolt tightening methods (e.g. manual, hydraulic, pneumatic, tensioning, etc.) Apply required bolt torque values.
WSO-PAGPS-0022 | Storage Pump 1 | PAG | Horizontal pump between bearings | Vibration dampers | Leaks due to deteriorated materials caused by fatigue | Medium | Age-related | Replace vibration dampers based on recommended life | Every 10 years | Maintenance contractor | Refer to recommended life of dampers by manufacturer. Otherwise, purchase spare damper before its recommended life to ensure availability when needed.
WSO-PAGPS-0022 | Storage Pump 1 | PAG | Horizontal pump between bearings | System | General system leaks | Low | Random | Inspect system for leaks | Shift | Operator | Report excessive leaks for scheduled repairs.
WSO-PAGPS-0022 | Storage Pump 1 | PAG | Horizontal pump between bearings | Impeller | Impeller wear | Low | Age-related | -Replace impeller -Inspect and measure clearances after every | -10 years -Annually | Maintenance contractor | Inspect during annual overhauls.
WSO-PAGPS-0022 | Storage Pump 1 | PAG | Horizontal pump between bearings | Suction strainer | Blockage | Medium | Age-related | Clean strainer | Annually | Maintenance contractor | During annual overhauls.
WSO-PAGPS-0033 | Storage Pump 2 | PAG | Horizontal pump between bearings | Bearings | Loss of lubrication | High | Age-related | Scheduled greasing | Weekly | Maintenance contractor | Avoid overgreasing. Use correct grease as stipulated by bearing manufacturer.
WSO-PAGPS-0033 | Storage Pump 2 | PAG | Horizontal pump between bearings | Bearings | High vibration due to cavitation | High | Random | Monitor suction pressure not to go below xx head. | Every hour | Operator | Refer to pump specifications on minimum NPSH requirements. Follow company policy in dealing with cavitation issues (e.g. call MCC to increase suction pressure and/or shutdown pumps)
WSO-PAGPS-0033 | Storage Pump 2 | PAG | Horizontal pump between bearings | Bearings | High vibration due to bearing failure (e.g. foreign materials in lubrication) | High | Random | Vibration monitoring | 2-weekly (every 2 weeks) | Maintenance contractor | Use trained contractor for the appropriate vibration monitoring device. Report findings every month.
WSO-PAGPS-0033 | Storage Pump 2 | PAG | Horizontal pump between bearings | Packing | Excessive leaks | Medium | Age-related | Tighten packing bolts | 2-weekly (every 2 weeks) | Maintenance contractor | Avoid overtightening of packing bolts.
WSO-PAGPS-0033 | Storage Pump 2 | PAG | Horizontal pump between bearings | Motor | Motor trip due to overloading | High | Random | Motor (skin) temperature measurement | Every hour | Operator | Refer to motor specifications on maximum allowable surface temperature.
WSO-PAGPS-0033 | Storage Pump 2 | PAG | Horizontal pump between bearings | Motor | Motor burns due to failure of winding insulation | Low | Age-related | Inspect motor winding insulation | Annually | Maintenance contractor | Use qualified maintenance contractor.
WSO-PAGPS-0033 | Storage Pump 2 | PAG | Horizontal pump between bearings | Suction isolating valve | Valve passing (leaks) | Medium | Age-related | Test valve integrity | Annually | Maintenance contractor | Use qualified maintenance contractor. Failure of this valve may cause problems during maintenance of pump/motor.
WSO-PAGPS-0033 | Storage Pump 2 | PAG | Horizontal pump between bearings | Discharge isolating valve | Valve passing (leaks) | Low | Age-related | Test valve integrity | Annually | Maintenance contractor | Use qualified maintenance contractor. Failure of this valve is not critical as long as the check valve is working.
WSO-PAGPS-0033 | Storage Pump 2 | PAG | Horizontal pump between bearings | Pressure gauge (suction & discharge) | Pressure gauge reading is wrong due to wear | Low | Age-related | Replace pressure gauge | Annually | Maintenance contractor | Replace with calibrated pressure gauge. Mark with acceptable operating range. Criticality is low if the online pressure sensors are still functioning properly.
WSO-PAGPS-0033 | Storage Pump 2 | PAG | Horizontal pump between bearings | Pressure sensors (suction & discharge) | Pressure reading is erroneous | High | Random | Calibrate pressure sensors | Semi-annually (every 6 months) | Maintenance contractor | Use qualified maintenance contractor.
WSO-PAGPS-0033 | Storage Pump 2 | PAG | Horizontal pump between bearings | Flange | Leaks due to loose bolts and/or gasket failure | Medium | Age-related | Re-tighten bolts using specified torque values | Annually | Maintenance contractor | Use proper bolt tightening methods (e.g. manual, hydraulic, pneumatic, tensioning, etc.) Apply required bolt torque values.
WSO-PAGPS-0033 | Storage Pump 2 | PAG | Horizontal pump between bearings | Vibration dampers | Leaks due to deteriorated materials caused by fatigue | Medium | Age-related | Replace vibration dampers based on recommended life | Every 10 years | Maintenance contractor | Refer to recommended life of dampers by manufacturer. Otherwise, purchase spare damper before its recommended life to ensure availability when needed.
WSO-PAGPS-0033 | Storage Pump 2 | PAG | Horizontal pump between bearings | System | General system leaks | Low | Random | Inspect system for leaks | Shift | Operator | Report excessive leaks for scheduled repairs.
WSO-PAGPS-0033 | Storage Pump 2 | PAG | Horizontal pump between bearings | Impeller | Impeller wear | Low | Age-related | -Replace impeller -Inspect and measure clearances after every | -10 years -Annually | Maintenance contractor | Inspect during annual overhauls.
WSO-PAGPS-0033 | Storage Pump 2 | PAG | Horizontal pump between bearings | Suction strainer | Blockage | Medium | Age-related | Clean strainer | Annually | Maintenance contractor | During annual overhauls.
WSO-PAGPS-0052 | Booster Pump 1 | PAG | Horizontal pump between bearings | Bearings | Loss of lubrication | High | Age-related | Scheduled greasing | Weekly | Maintenance contractor | Avoid overgreasing. Use correct grease as stipulated by bearing manufacturer.
WSO-PAGPS-0052 | Booster Pump 1 | PAG | Horizontal pump between bearings | Bearings | High vibration due to cavitation | High | Random | Monitor suction pressure not to go below xx head. | Every hour | Operator | Refer to pump specifications on minimum NPSH requirements. Follow company policy in dealing with cavitation issues (e.g. call MCC to increase suction pressure and/or shutdown pumps)
WSO-PAGPS-0052 | Booster Pump 1 | PAG | Horizontal pump between bearings | Bearings | High vibration due to bearing failure (e.g. foreign materials in lubrication) | High | Random | Vibration monitoring | 2-weekly (every 2 weeks) | Maintenance contractor | Use trained contractor for the appropriate vibration monitoring device. Report findings every month.
WSO-PAGPS-0052 | Booster Pump 1 | PAG | Horizontal pump between bearings | Packing | Excessive leaks | Medium | Age-related | Tighten packing bolts | 2-weekly (every 2 weeks) | Maintenance contractor | Avoid overtightening of packing bolts.
WSO-PAGPS-0052 | Booster Pump 1 | PAG | Horizontal pump between bearings | Motor | Motor trip due to overloading | High | Random | Motor (skin) temperature measurement | Every hour | Operator | Refer to motor specifications on maximum allowable surface temperature.
WSO-PAGPS-0052 | Booster Pump 1 | PAG | Horizontal pump between bearings | Motor | Motor burns due to failure of winding insulation | Low | Age-related | Inspect motor winding insulation | Annually | Maintenance contractor | Use qualified maintenance contractor.
WSO-PAGPS-0052 | Booster Pump 1 | PAG | Horizontal pump between bearings | Suction isolating valve | Valve passing (leaks) | Medium | Age-related | Test valve integrity | Annually | Maintenance contractor | Use qualified maintenance contractor. Failure of this valve may cause problems during maintenance of pump/motor.
WSO-PAGPS-0052 | Booster Pump 1 | PAG | Horizontal pump between bearings | Discharge isolating valve | Valve passing (leaks) | Low | Age-related | Test valve integrity | Annually | Maintenance contractor | Use qualified maintenance contractor. Failure of this valve is not critical as long as the check valve is working.
WSO-PAGPS-0052 | Booster Pump 1 | PAG | Horizontal pump between bearings | Pressure gauge (suction & discharge) | Pressure gauge reading is wrong due to wear | Low | Age-related | Replace pressure gauge | Annually | Maintenance contractor | Replace with calibrated pressure gauge. Mark with acceptable operating range. Criticality is low if the online pressure sensors are still functioning properly.
WSO-PAGPS-0052 | Booster Pump 1 | PAG | Horizontal pump between bearings | Pressure sensors (suction & discharge) | Pressure reading is erroneous | High | Random | Calibrate pressure sensors | Semi-annually (every 6 months) | Maintenance contractor | Use qualified maintenance contractor.
WSO-PAGPS-0052 | Booster Pump 1 | PAG | Horizontal pump between bearings | Flange | Leaks due to loose bolts and/or gasket failure | Medium | Age-related | Re-tighten bolts using specified torque values | Annually | Maintenance contractor | Use proper bolt tightening methods (e.g. manual, hydraulic, pneumatic, tensioning, etc.) Apply required bolt torque values.
WSO-PAGPS-0052 | Booster Pump 1 | PAG | Horizontal pump between bearings | Vibration dampers | Leaks due to deteriorated materials caused by fatigue | Medium | Age-related | Replace vibration dampers based on recommended life | Every 10 years | Maintenance contractor | Refer to recommended life of dampers by manufacturer. Otherwise, purchase spare damper before its recommended life to ensure availability when needed.
WSO-PAGPS-0052 | Booster Pump 1 | PAG | Horizontal pump between bearings | System | General system leaks | Low | Random | Inspect system for leaks | Shift | Operator | Report excessive leaks for scheduled repairs.
WSO-PAGPS-0052 | Booster Pump 1 | PAG | Horizontal pump between bearings | Impeller | Impeller wear | Low | Age-related | -Replace impeller -Inspect and measure clearances after every | -10 years -Annually | Maintenance contractor | Inspect during annual overhauls.
WSO-PAGPS-0052 | Booster Pump 1 | PAG | Horizontal pump between bearings | Suction strainer | Blockage | Medium | Age-related | Clean strainer | Annually | Maintenance contractor | During annual overhauls.
WSO-PAGPS-0062 | Booster Pump 2 | PAG | Horizontal pump between bearings | Bearings | Loss of lubrication | High | Age-related | Scheduled greasing | Weekly | Maintenance contractor | Avoid overgreasing. Use correct grease as stipulated by bearing manufacturer.
WSO-PAGPS-0063 | Booster Pump 2 | PAG | Horizontal pump between bearings | Bearings | High vibration due to cavitation | High | Random | Monitor suction pressure not to go below xx head. | Every hour | Operator | Refer to pump specifications on minimum NPSH requirements. Follow company policy in dealing with cavitation issues (e.g. call MCC to increase suction pressure and/or shutdown pumps)
WSO-PAGPS-0064 | Booster Pump 2 | PAG | Horizontal pump between bearings | Bearings | High vibration due to bearing failure (e.g. foreign materials in lubrication) | High | Random | Vibration monitoring | 2-weekly (every 2 weeks) | Maintenance contractor | Use trained contractor for the appropriate vibration monitoring device. Report findings every month.
WSO-PAGPS-0065 | Booster Pump 2 | PAG | Horizontal pump between bearings | Packing | Excessive leaks | Medium | Age-related | Tighten packing bolts | 2-weekly (every 2 weeks) | Maintenance contractor | Avoid overtightening of packing bolts.
WSO-PAGPS-0066 | Booster Pump 2 | PAG | Horizontal pump between bearings | Motor | Motor trip due to overloading | High | Random | Motor (skin) temperature measurement | Every hour | Operator | Refer to motor specifications on maximum allowable surface temperature.
WSO-PAGPS-0067 | Booster Pump 2 | PAG | Horizontal pump between bearings | Motor | Motor burns due to failure of winding insulation | Low | Age-related | Inspect motor winding insulation | Annually | Maintenance contractor | Use qualified maintenance contractor.
WSO-PAGPS-0068 | Booster Pump 2 | PAG | Horizontal pump between bearings | Suction isolating valve | Valve passing (leaks) | Medium | Age-related | Test valve integrity | Annually | Maintenance contractor | Use qualified maintenance contractor. Failure of this valve may cause problems during maintenance of pump/motor.
WSO-PAGPS-0069 | Booster Pump 2 | PAG | Horizontal pump between bearings | Discharge isolating valve | Valve passing (leaks) | Low | Age-related | Test valve integrity | Annually | Maintenance contractor | Use qualified maintenance contractor. Failure of this valve is not critical as long as the check valve is working.
WSO-PAGPS-0070 | Booster Pump 2 | PAG | Horizontal pump between bearings | Pressure gauge (suction & discharge) | Pressure gauge reading is wrong due to wear | Low | Age-related | Replace pressure gauge | Annually | Maintenance contractor | Replace with calibrated pressure gauge. Mark with acceptable operating range. Criticality is low if the online pressure sensors are still functioning properly.
WSO-PAGPS-0071 | Booster Pump 2 | PAG | Horizontal pump between bearings | Pressure sensors (suction & discharge) | Pressure reading is erroneous | High | Random | Calibrate pressure sensors | Semi-annually (every 6 months) | Maintenance contractor | Use qualified maintenance contractor.
WSO-PAGPS-0072 | Booster Pump 2 | PAG | Horizontal pump between bearings | Flange | Leaks due to loose bolts and/or gasket failure | Medium | Age-related | Re-tighten bolts using specified torque values | Annually | Maintenance contractor | Use proper bolt tightening methods (e.g. manual, hydraulic, pneumatic, tensioning, etc.) Apply required bolt torque values.
WSO-PAGPS-0073 | Booster Pump 2 | PAG | Horizontal pump between bearings | Vibration dampers | Leaks due to deteriorated materials caused by fatigue | Medium | Age-related | Replace vibration dampers based on recommended life | Every 10 years | Maintenance contractor | Refer to recommended life of dampers by manufacturer. Otherwise, purchase spare damper before its recommended life to ensure availability when needed.
WSO-PAGPS-0074 | Booster Pump 2 | PAG | Horizontal pump between bearings | System | General system leaks | Low | Random | Inspect system for leaks | Shift | Operator | Report excessive leaks for scheduled repairs.
WSO-PAGPS-0075 | Booster Pump 2 | PAG | Horizontal pump between bearings | Impeller | Impeller wear | Low | Age-related | -Replace impeller -Inspect and measure clearances after every | -10 years -Annually | Maintenance contractor | Inspect during annual overhauls.
WSO-PAGPS-0076 | Booster Pump 2 | PAG | Horizontal pump between bearings | Suction strainer | Blockage | Medium | Age-related | Clean strainer | Annually | Maintenance contractor | During annual overhauls.
WSO-PAGPS-0072 | Booster Pump 3 | PAG | Horizontal pump between bearings | Bearings | Loss of lubrication | High | Age-related | Scheduled greasing | Weekly | Maintenance contractor | Avoid overgreasing. Use correct grease as stipulated by bearing manufacturer.
WSO-PAGPS-0072 | Booster Pump 3 | PAG | Horizontal pump between bearings | Bearings | High vibration due to cavitation | High | Random | Monitor suction pressure not to go below xx head. | Every hour | Operator | Refer to pump specifications on minimum NPSH requirements. Follow company policy in dealing with cavitation issues (e.g. call MCC to increase suction pressure and/or shutdown pumps)
WSO-PAGPS-0072 | Booster Pump 3 | PAG | Horizontal pump between bearings | Bearings | High vibration due to bearing failure (e.g. foreign materials in lubrication) | High | Random | Vibration monitoring | 2-weekly (every 2 weeks) | Maintenance contractor | Use trained contractor for the appropriate vibration monitoring device. Report findings every month.
WSO-PAGPS-0072 | Booster Pump 3 | PAG | Horizontal pump between bearings | Packing | Excessive leaks | Medium | Age-related | Tighten packing bolts | 2-weekly (every 2 weeks) | Maintenance contractor | Avoid overtightening of packing bolts.
WSO-PAGPS-0072 | Booster Pump 3 | PAG | Horizontal pump between bearings | Motor | Motor trip due to overloading | High | Random | Motor (skin) temperature measurement | Every hour | Operator | Refer to motor specifications on maximum allowable surface temperature.
WSO-PAGPS-0072 | Booster Pump 3 | PAG | Horizontal pump between bearings | Motor | Motor burns due to failure of winding insulation | Low | Age-related | Inspect motor winding insulation | Annually | Maintenance contractor | Use qualified maintenance contractor.
WSO-PAGPS-0072 | Booster Pump 3 | PAG | Horizontal pump between bearings | Suction isolating valve | Valve passing (leaks) | Medium | Age-related | Test valve integrity | Annually | Maintenance contractor | Use qualified maintenance contractor. Failure of this valve may cause problems during maintenance of pump/motor.
WSO-PAGPS-0072 | Booster Pump 3 | PAG | Horizontal pump between bearings | Discharge isolating valve | Valve passing (leaks) | Low | Age-related | Test valve integrity | Annually | Maintenance contractor | Use qualified maintenance contractor. Failure of this valve is not critical as long as the check valve is working.
WSO-PAGPS-0072 | Booster Pump 3 | PAG | Horizontal pump between bearings | Pressure gauge (suction & discharge) | Pressure gauge reading is wrong due to wear | Low | Age-related | Replace pressure gauge | Annually | Maintenance contractor | Replace with calibrated pressure gauge. Mark with acceptable operating range. Criticality is low if the online pressure sensors are still functioning properly.
WSO-PAGPS-0072 | Booster Pump 3 | PAG | Horizontal pump between bearings | Pressure sensors (suction & discharge) | Pressure reading is erroneous | High | Random | Calibrate pressure sensors | Semi-annually (every 6 months) | Maintenance contractor | Use qualified maintenance contractor.
WSO-PAGPS-0072 | Booster Pump 3 | PAG | Horizontal pump between bearings | Flange | Leaks due to loose bolts and/or gasket failure | Medium | Age-related | Re-tighten bolts using specified torque values | Annually | Maintenance contractor | Use proper bolt tightening methods (e.g. manual, hydraulic, pneumatic, tensioning, etc.) Apply required bolt torque values.
WSO-PAGPS-0072 | Booster Pump 3 | PAG | Horizontal pump between bearings | Vibration dampers | Leaks due to deteriorated materials caused by fatigue | Medium | Age-related | Replace vibration dampers based on recommended life | Every 10 years | Maintenance contractor | Refer to recommended life of dampers by manufacturer. Otherwise, purchase spare damper before its recommended life to ensure availability when needed.
WSO-PAGPS-0072 | Booster Pump 3 | PAG | Horizontal pump between bearings | System | General system leaks | Low | Random | Inspect system for leaks | Shift | Operator | Report excessive leaks for scheduled repairs.
WSO-PAGPS-0072 | Booster Pump 3 | PAG | Horizontal pump between bearings | Impeller | Impeller wear | Low | Age-related | -Replace impeller -Inspect and measure clearances after every | -10 years -Annually | Maintenance contractor | Inspect during annual overhauls.
WSO-PAGPS-0072 | Booster Pump 3 | PAG | Horizontal pump between bearings | Suction strainer | Blockage | Medium | Age-related | Clean strainer | Annually | Maintenance contractor | During annual overhauls.
WSO-PAGPS-0082 | Booster Pump 4 | PAG | Horizontal pump between bearings | Bearings | Loss of lubrication | High | Age-related | Scheduled greasing | Weekly | Maintenance contractor | Avoid overgreasing. Use correct grease as stipulated by bearing manufacturer.
WSO-PAGPS-0082 | Booster Pump 4 | PAG | Horizontal pump between bearings | Bearings | High vibration due to cavitation | High | Random | Monitor suction pressure not to go below xx head. | Every hour | Operator | Refer to pump specifications on minimum NPSH requirements. Follow company policy in dealing with cavitation issues (e.g. call MCC to increase suction pressure and/or shutdown pumps)
WSO-PAGPS-0082 | Booster Pump 4 | PAG | Horizontal pump between bearings | Bearings | High vibration due to bearing failure (e.g. foreign materials in lubrication) | High | Random | Vibration monitoring | 2-weekly (every 2 weeks) | Maintenance contractor | Use trained contractor for the appropriate vibration monitoring device. Report findings every month.
WSO-PAGPS-0082 | Booster Pump 4 | PAG | Horizontal pump between bearings | Packing | Excessive leaks | Medium | Age-related | Tighten packing bolts | 2-weekly (every 2 weeks) | Maintenance contractor | Avoid overtightening of packing bolts.
WSO-PAGPS-0082 | Booster Pump 4 | PAG | Horizontal pump between bearings | Motor | Motor trip due to overloading | High | Random | Motor (skin) temperature measurement | Every hour | Operator | Refer to motor specifications on maximum allowable surface temperature.
WSO-PAGPS-0082 | Booster Pump 4 | PAG | Horizontal pump between bearings | Motor | Motor burns due to failure of winding insulation | Low | Age-related | Inspect motor winding insulation | Annually | Maintenance contractor | Use qualified maintenance contractor.
WSO-PAGPS-0082 | Booster Pump 4 | PAG | Horizontal pump between bearings | Suction isolating valve | Valve passing (leaks) | Medium | Age-related | Test valve integrity | Annually | Maintenance contractor | Use qualified maintenance contractor. Failure of this valve may cause problems during maintenance of pump/motor.
WSO-PAGPS-0082 | Booster Pump 4 | PAG | Horizontal pump between bearings | Discharge isolating valve | Valve passing (leaks) | Low | Age-related | Test valve integrity | Annually | Maintenance contractor | Use qualified maintenance contractor. Failure of this valve is not critical as long as the check valve is working.
WSO-PAGPS-0082 | Booster Pump 4 | PAG | Horizontal pump between bearings | Pressure gauge (suction & discharge) | Pressure gauge reading is wrong due to wear | Low | Age-related | Replace pressure gauge | Annually | Maintenance contractor | Replace with calibrated pressure gauge. Mark with acceptable operating range. Criticality is low if the online pressure sensors are still functioning properly.
WSO-PAGPS-0082 | Booster Pump 4 | PAG | Horizontal pump between bearings | Pressure sensors (suction & discharge) | Pressure reading is erroneous | High | Random | Calibrate pressure sensors | Semi-annually (every 6 months) | Maintenance contractor | Use qualified maintenance contractor.
WSO-PAGPS-0082 | Booster Pump 4 | PAG | Horizontal pump between bearings | Flange | Leaks due to loose bolts and/or gasket failure | Medium | Age-related | Re-tighten bolts using specified torque values | Annually | Maintenance contractor | Use proper bolt tightening methods (e.g. manual, hydraulic, pneumatic, tensioning, etc.) Apply required bolt torque values.
WSO-PAGPS-0082 | Booster Pump 4 | PAG | Horizontal pump between bearings | Vibration dampers | Leaks due to deteriorated materials caused by fatigue | Medium | Age-related | Replace vibration dampers based on recommended life | Every 10 years | Maintenance contractor | Refer to recommended life of dampers by manufacturer. Otherwise, purchase spare damper before its recommended life to ensure availability when needed.
WSO-PAGPS-0082 | Booster Pump 4 | PAG | Horizontal pump between bearings | System | General system leaks | Low | Random | Inspect system for leaks | Shift | Operator | Report excessive leaks for scheduled repairs.
WSO-PAGPS-0082 | Booster Pump 4 | PAG | Horizontal pump between bearings | Impeller | Impeller wear | Low | Age-related | -Replace impeller -Inspect and measure clearances after every | -10 years -Annually | Maintenance contractor | Inspect during annual overhauls.
WSO-PAGPS-0082 | Booster Pump 4 | PAG | Horizontal pump between bearings | Suction strainer | Blockage | Medium | Age-related | Clean strainer | Annually | Maintenance contractor | During annual overhauls.
WSO-PAGPS-0092 | Booster Pump 5 | PAG | Horizontal pump between bearings | Bearings | Loss of lubrication | High | Age-related | Scheduled greasing | Weekly | Maintenance contractor | Avoid overgreasing. Use correct grease as stipulated by bearing manufacturer.
WSO-PAGPS-0092 | Booster Pump 5 | PAG | Horizontal pump between bearings | Bearings | High vibration due to cavitation | High | Random | Monitor suction pressure not to go below xx head. | Every hour | Operator | Refer to pump specifications on minimum NPSH requirements. Follow company policy in dealing with cavitation issues (e.g. call MCC to increase suction pressure and/or shutdown pumps)
WSO-PAGPS-0092 | Booster Pump 5 | PAG | Horizontal pump between bearings | Bearings | High vibration due to bearing failure (e.g. foreign materials in lubrication) | High | Random | Vibration monitoring | 2-weekly (every 2 weeks) | Maintenance contractor | Use trained contractor for the appropriate vibration monitoring device. Report findings every month.
WSO-PAGPS-0092 | Booster Pump 5 | PAG | Horizontal pump between bearings | Packing | Excessive leaks | Medium | Age-related | Tighten packing bolts | 2-weekly (every 2 weeks) | Maintenance contractor | Avoid overtightening of packing bolts.
WSO-PAGPS-0092 | Booster Pump 5 | PAG | Horizontal pump between bearings | Motor | Motor trip due to overloading | High | Random | Motor (skin) temperature measurement | Every hour | Operator | Refer to motor specifications on maximum allowable surface temperature.
WSO-PAGPS-0092 | Booster Pump 5 | PAG | Horizontal pump between bearings | Motor | Motor burns due to failure of winding insulation | Low | Age-related | Inspect motor winding insulation | Annually | Maintenance contractor | Use qualified maintenance contractor.
WSO-PAGPS-0092 | Booster Pump 5 | PAG | Horizontal pump between bearings | Suction isolating valve | Valve passing (leaks) | Medium | Age-related | Test valve integrity | Annually | Maintenance contractor | Use qualified maintenance contractor. Failure of this valve may cause problems during maintenance of pump/motor.
WSO-PAGPS-0092 | Booster Pump 5 | PAG | Horizontal pump between bearings | Discharge isolating valve | Valve passing (leaks) | Low | Age-related | Test valve integrity | Annually | Maintenance contractor | Use qualified maintenance contractor. Failure of this valve is not critical as long as the check valve is working.
WSO-PAGPS-0092 | Booster Pump 5 | PAG | Horizontal pump between bearings | Pressure gauge (suction & discharge) | Pressure gauge reading is wrong due to wear | Low | Age-related | Replace pressure gauge | Annually | Maintenance contractor | Replace with calibrated pressure gauge. Mark with acceptable operating range. Criticality is low if the online pressure sensors are still functioning properly.
WSO-PAGPS-0092 | Booster Pump 5 | PAG | Horizontal pump between bearings | Pressure sensors (suction & discharge) | Pressure reading is erroneous | High | Random | Calibrate pressure sensors | Semi-annually (every 6 months) | Maintenance contractor | Use qualified maintenance contractor.
WSO-PAGPS-0092 | Booster Pump 5 | PAG | Horizontal pump between bearings | Flange | Leaks due to loose bolts and/or gasket failure | Medium | Age-related | Re-tighten bolts using specified torque values | Annually | Maintenance contractor | Use proper bolt tightening methods (e.g. manual, hydraulic, pneumatic, tensioning, etc.) Apply required bolt torque values.
WSO-PAGPS-0092 | Booster Pump 5 | PAG | Horizontal pump between bearings | Vibration dampers | Leaks due to deteriorated materials caused by fatigue | Medium | Age-related | Replace vibration dampers based on recommended life | Every 10 years | Maintenance contractor | Refer to recommended life of dampers by manufacturer. Otherwise, purchase spare damper before its recommended life to ensure availability when needed.
WSO-PAGPS-0092 | Booster Pump 5 | PAG | Horizontal pump between bearings | System | General system leaks | Low | Random | Inspect system for leaks | Shift | Operator | Report excessive leaks for scheduled repairs.
WSO-PAGPS-0092 | Booster Pump 5 | PAG | Horizontal pump between bearings | Impeller | Impeller wear | Low | Age-related | -Replace impeller -Inspect and measure clearances after every | -10 years -Annually | Maintenance contractor | Inspect during annual overhauls.
WSO-PAGPS-0092 | Booster Pump 5 | PAG | Horizontal pump between bearings | Suction strainer | Blockage | Medium | Age-related | Clean strainer | Annually | Maintenance contractor | During annual overhauls.
WSO-PAGPS-0102 | Booster Pump 6 - SPARE (dedicated) | PAG | Horizontal pump between bearings | Bearings | bearing failure caused by false brinelling | High | Age-related | Rotate pump shaft 2-1/4 times | Every shift | Operator | Ensure that pump is isolated from power source
WSO-PAGPS-0102 | Booster Pump 6 - SPARE (dedicated) | PAG | Horizontal pump between bearings | Bearings | Bearing failure caused by contaminated oil | High | Random | Inspect oil for water contamination Regrease as necessary | Weekly | Maintenance contractor
WSO-PAGPS-0102 | Booster Pump 6 - SPARE (dedicated) | PAG | Horizontal pump between bearings | Starter; Auto start system | Fail to start | High | Random | Start pump and run for at least 2 hours. Check all functionalities. | Monthly | Operator | Do this during visit by maintenance contractor.
The list represents an initial recommended maintenance program for the mechanical (including motors and instruments) assets in Pagcor Pumping Facilities. The methodology used in its development is RCM (Reliability-Centered Maintenance). It is not intended to be the final list and should be treated as a "living" program. This simply means that it should always be reviewed and continuously improved over time. However, in doing this, the organization responsible for its sustainability should be aware of the methodologies and concepts used in RCM.
CRITICALITY MATRIX (Generic)
CONSEQUENCES | PROBABILITY
High (product not delivered)
Medium (reduced delivery of product)
Low (low of minimum operational interruption)
| Low | Medium | High
| <20%/yr | 20-80%/yr | >80%/yr
Criticality:
High
Medium
Low